## 使用说明
机型功率： | 50 | KW | 按机器最大功率段填写 |  |  | 版本号： | V1.3.2
注意事项：
1.安规库版本号只需要修改使能位L列第二行
2.请特别注意参数的单位（在第2行做说明）
3.使用导文件的时候不能同时打开excel，会出现闪退现象
4.测试部人员添加测试标准行，可不填写国家值，会自动跳过，但一定注意不能填充前面的使能位数值，会影响下面使能位的生成
5.DCI保护参数 和 ISO孤岛参数 不通用！不通用！不通用！！！！！需要根据机型修改
6.【使用说明】页机型功率注意修改
安规文件参数填写标准：
1.当某个安规文件的安规编号、国家、标准地区编码不一致时，会导致求校准错误无法生成正确文件
2.当输入的数值除以精度得到的结果大于65535时，系统将自动匹配为最大值（65535）存储
3.当输入的数值除以精度得到的结果为浮点数时，系统将自动匹配取整数位存储
4.第二页工作表筛选国家不为空值数据，不显示（导入功能）
升版：
如果有参数或格式需要更改，请在下面表格中填写相关信息。
制定时间 |  | 版本号 |  | 修改内容 | 修改人
2023-12-25 |  | V5.9 |  | 1、修改019-000欧洲-IEC EN61727电压参数 2、修改020-000韩国电压参数、频率参数 3、修改西班牙（003-000、003-003、003-004、003-005）电压穿越参数 4、修改丹麦（005-001）、印度（025-000、025-003、025-004、025-005）无功参数 5、修改德国VDE4105（000-000）启动参数 6、修改中国CQC A类010-009频率参数 7、修改西班牙UNE+RD 003-003电压参数 8、修改立陶宛108-000频率参数 9、修改所有未使用但初值为0不符合Modbus协议规定取值范围的参数 10、修改德国（000-000、000-001、000-002、000-006）、奥地利TOR（013-000）ISO孤岛参数 11、修改中国宽范围电压010-012启动参数、电压参数 | 赵佳宝
2023-12-13 |  | V5.8 |  | 1、修改020-000韩国无功参数、电压参数、频率参数、DCI保护参数、频率有功参数 2、修改026-000菲律宾PHI频率有功、无功参数 3、修改026-002菲律宾-低压、046-000迪拜-低压、046-001迪拜-中压、011-000法国VDE0126、011-003法国VFR 2019、012-000波兰A、012-003波兰ABCD、123-000罗马尼亚、000-001德国BDEW、000-002德国VDE40126、000-005德国VDE4110、000-006德国VDE4120、西班牙（003-000、003-003、003-004、003-005）、009-000英国G99、009-001英国G98、巴西（028-000、028-001、028-002、028-003）、北爱尔兰G99、G98（039-002、039-003）无功参数 4、修改010-009中国CQC A类启动参数、010-000中国CQC B类频率参数 5、修改001-000意大利频率有功参数、远程及有功参数，001-001意大利频率有功参数，001-003意大利DCI保护参数 6、修改025-003印度CEA频率保护参数 7、修改004-000土耳其、005-000丹麦远程及有功参数，005-001丹麦TR322、005-003丹麦东部频率有功参数 8、根据V09安规库频率参数页新增bit6频率变化率保护使能位 | 赵佳宝
2023-12-01 |  | V5.7 |  | 1、修改000-000德国VDE4105无功参数 2、修改001-001意大利0-16无功参数 3、修改040-000、040-001泰国PEA、MEA频率参数、无功参数、电压参数 4、修改003-002西班牙NTS频率有功参数、电压穿越参数、无功参数 5、修改009-000、009-001英国G99、G98电压穿越参数、039-002、039-003北爱尔兰G99、G98电压穿越参数 6、修改039-000、039-001爱尔兰频率参数、电压参数、频率有功参数 7、修改018-003 欧洲通用电压穿越参数 8、修改002-008、002-009澳大利亚B、C频率有功参数 9、修改027-000 新西兰频率有功参数 10、修改046-000、046-001迪拜频率有功参数 11、修改026-000电压穿越参数 | 李琴
2023-11-23 |  | V5.6 |  | 1、修改009-000、009-001 英国G99/G98安规启动参数、频率有功参数、电压穿越参数 2、修改039-002、039-003北爱尔兰G99/G98安规启动参数、频率有功参数、电压穿越参数 3、修改028-000、028-001、028-002、028-003巴西安规频率有功参数 4、修改013-000奥地利安规无功参数 5、修改无功参数页Bit10为按最大相电压控制使能位 | 李琴
2023-11-15 |  | V5.5 |  | 1、新增010-012中国宽范围电压安规 2、修改013-000奥地利安规最大超前无功功率百分比为43.6% | 李琴
2023-11-14 |  | V5.4 |  | 1、修改123-000罗马尼亚安规频率有功参数Bit4过频从额定功率开始降载使能位为失能 2、修改024-001、024-002、024-003塞浦路斯等级A、B、C安规启动参数、频率有功参数、电压穿越参数 | 李琴
2023-11-09 |  | V5.3 |  | 1、增加025-005印度-Kerala安规 | 李琴
2023-11-06 |  | V5.2 |  | 1、根据09安规库新增频率有功参数页新增Bit14过频降载功率截止使能位，028-000巴西安规默认使能 2、000-005德国4110安规电压穿越参数页Bit6、Bit7、Bit8默认使能 | 李琴
2023-11-01 |  | V5.1 |  | 1、增加024-001塞浦路斯等级A安规 2、增加024-002塞浦路斯等级B安规 3、增加024-003塞浦路斯等级C安规 4、修改024-000塞浦路斯安规启动/重连电网电压下限标准、一级欠压保护值标准 5、修改123-000罗马尼亚频率有功参数过频回载前等待时间及过频降载回载频率 6、修改参数版本为900 | 李琴
2023-10-30 |  | V5.0 |  | 1、根据09安规库新增频率参数页频率变化率保护值、保护时间 2、根据09安规库新增远程有功参数页Bit10CLS防逆流使能位、CLS远程配置、CLS防逆流输出/输入电流限制百分比、CLS防逆流PCC电流限制/保护时间 3、根据09安规库新增频率有功参数页Bit9过欠频回载速率使能位 4、根据09安规库新增电压穿越参数页Bit7低穿有功使能位、高穿有功功率起始电压值百分比、低穿有功功率起始电压值百分比 5、根据09安规库新增ISO孤岛参数页新增SpecialCertification | 李琴
2023-10-20 |  | V4.8 |  | 1、修改123-000罗马尼亚安规频率有功参数Bit4过频从额定功率开始降载使能位为使能 | 李琴
2023-10-18 |  | V4.7 |  | 1、修改015-000、015-001瑞士A、瑞士B的DCI一级保护值、二级保护值、二级保护时间 2、修改125-000芬兰安规欠频起始频率与欠频降载斜率百分比 3、修改奥地利013-000无功参数Bit1、Bit2为使能，修改最大超前无功功率百分比为48.43% | 李琴
2023-10-11 |  | V4.6 |  | 1、增加003-005西班牙低压安规 2、增加008-002比利时低压安规 3、增加125-000芬兰安规 4、修改034-001挪威低压启动参数、频率参数 | 李琴
2023-09-26 |  | V4.5 |  | 1、增加112-000智利安规 2、000-000德国4105过压一级使能位改为禁能 3、修改000-000、000-001、000-002、000-005、000-006远程有功参数逻辑接口1对应功率为0 4、根据安规参数更改登记表更改部分标准形式（参数未变更） | 李琴
2023-09-12 |  | V4.4 |  | 1、修改030-004捷克PPDS 2023 安规电压穿越参数进入低穿电压值百分比 2、修改030-003捷克安规有功输出百分比 3、增加124-000突尼斯安规 4、修改电压标准表现形式为Un% | 李琴
2023-09-11 |  | V4.3 |  | 1、修改001-003意大利安规电压参数 2、修改030-004捷克PPDS 2023安规电压穿越参数进入高穿电压百分比、高穿退出电压百分比 | 李琴
2023-08-30 |  | V4.2 |  | 1、增加011-008 法国EN50549-2安规 2、增加018-003 欧洲EN50549-2安规 3、增加030-004 捷克 PPDS 2023安规（≥0.8kW且<100kW) 4、增加044-002 南非+RPPS of Category C安规 5、修改德国VDE4110、德国VDE4120电压穿越参数 6、修改013-000奥地利、011-007法国EN50549-1无功参数 | 李琴
2023-08-17 |  | V4.1 |  | 1、增加011-007 法国EN50549-1安规 2、增加025-004印度IEC61727-LV安规 3、修改028-001、-28-002、028-003巴西安规启动参数、电压参数、频率参数、频率有功参数 4、修改001-000、001-002意大利0-21、025-000印度、019-000 DCI保护参数 | 李琴
2023-08-03 |  | V4.0 |  | 1、修改030-000捷克安规电压参数总使能位为75 | 李琴
2023-07-21 |  | V3.9 |  | 1、040-000泰国PEA、040-001泰国MEA的低穿高穿使能位改为默认使能 | 李琴
2023-07-10 |  | V3.8 |  | 1、013-000奥地利安规无功参数Bit2、Bit10无功模式四奥地利使能位禁能 2、修改剩下部分安规国家的高压穿越退出电压值百分比为进入高穿电压值百分比-1% 3、000-000德国4105、003-002西班牙NTS、044-000南非电压穿越参数负序电流使能位使能 | 李琴
2023-06-19 |  | V3.7 |  | 1、增加010-011东方日升安规 | 李琴
2023-06-15 |  | V3.6 |  | 1、修改捷克030-001~003高低穿部分参数 2、修改斯洛文尼亚进入低穿电压值百分比、高穿第三点电压百分比 | 李琴
2023-06-07 |  | V3.5 |  | 1、修改001-000意大利（0-21）内部频率有功参数、电压穿越参数 2、修改030-003捷克(>16A系统)电压穿越页高/低穿无功电流系数K为公式（<=100KW系统K值为0，>100KW系统K值为2） 3、修改大部分国家低穿退出点为进入点+1%，高穿退出点为进入点-1% 4、修改031-000斯洛文尼亚高/低穿第四点电压百分比 | 李琴
2023-06-07 |  | V3.4 |  | 1、修改012-000波兰A、012-003波兰ABCD远程及有功参数中的过压降载使能、截止功率、速率，逻辑接口1-8对应功率、逻辑接口降载速率;频率有功参数中过频回载前等待时间；无功参数中无功模式使能、无功模式4 Lockin功率值百分比、Lockout功率值百分比；电压穿越参数中OVRT使能、负序电流使能，低穿第四点百分比，高/低穿无功电流系数K，零电流进入高/低电压百分比，高/低穿退出电压值百分比，高/低穿无功电流计算起始电压值百分比 2、010-009中国CQCA类过频输出降载使能、过频回载使能 3、修改123-000罗马尼亚启动、重连功率上升速率为10%Pn | 李琴
2023-05-26 |  | V3.3 |  | 1、001-000、001-001 并网前等待时间改为300s 2、原001-004标准名称改为CEI-016-HV 意大利(0-16)-高压 3、原001-005标准名称改为CEI-016-MV 意大利(0-16)-中压 4、插入（预留）001-004 CEI-021In.-HV 意大利(0-21)内部-高压，原001-004、001-005后移为001-005、001-006 5、增加109-000 爱沙尼亚安规 6、028-000巴西标准名称修改为PORTARIA Nº 140 7、028-000巴西过频降载斜率百分比增加备注：(60.2Hz-62.6Hz频率段有功功率按30%Pn/Hz降载到28%Pn，62.6Hz-63.1Hz有功功率不再随着频率变化) | 李琴
2023-05-12 |  | V3.2 |  | 1、018-001、039-000、039-001 、007-000、004-000过频回载前等待时间修改为35000ms、过频降载回载频率修改为50.1HZ 2、土耳其、丹麦、希腊、荷兰、比利时、欧洲EN50549、捷克、斯洛文尼亚、爱尔兰等国家安规无功模式4最大超前/滞后无功功率百分比修改为48.43%Pn 3、020-001韩国DASS有功降载改为不使能，有功输出修改为100% | 李琴
2023-04-13 |  | V3.1 |  | 1、修改013-000奥地利TOR安规（一二级过欠压保护时间、一级过欠频保护时间、无功模式4最大滞后无功功率百分比改为43.6%Pn） | 李琴
2023-03-21 |  | V3.0 |  | 1、ISO孤岛参数页增加 PE和N控制寄存器总使能位及相应bit使能位 (Bit0:离网PEN短接使能位 Bit1:N线检测使能位) | 李琴
2023-03-16 |  | V2.9 |  | 1、增加030-002捷克安规（用于<=16A系统） 2、增加030-003捷克安规（用于>16A系统） 3、修改013-000奥地利TOR安规（一二级过欠压保护时间、一级过欠频保护时间、无功模式4最大超前无功功率百分比改为43.6%、零电流模式进入高低电压百分比分别改为115%Un和85%Un） | 李琴
2023-03-10 |  | V2.8 |  | 1、修改030-001捷克中压标准名称为Czechia-MV | 李琴
2023-03-06 |  | V2.7 |  | 1、增加法国011-004 VDE0126 Enedis安规 2、增加法国011-005 VDE0126-HV Enedis安规 3、增加法国011-006 VFR2019 Enedis安规 4、增加026-002 菲律宾低压安规 5、增加031-000 斯洛文尼亚50549安规 | 李琴
2023-02-27 |  | V2.6 |  | 1、增加德国4110安规 2、增加德国4120安规 3、根据08安规库新增高穿有功使能位(010-000中国默认使能) | 李琴
2023-02-01 |  | V2.5 |  | 1、修改001-000、001-001、001-003、001-004、001-005意大利参数 | 李琴
2022-12-21 |  | V2.4 |  | 1.新增039-001爱尔兰区分参数 2.新增039-002北爱尔兰G99安规 3.新增039-003北爱尔兰G98安规 | 李琴
2022-12-14 |  | V2.3 |  | 1、修改001-001意大利参数 2、修改丹麦东部、西部参数 | 侯意
2022-12-13 |  | V2.2 |  | 1、根据08安规库新增过欠压、过欠频保护时间高位，远程开关机速率使能位，欠频降载方式使能位，高穿有功使能位 | 侯意
2022-12-06 |  | V2.1 |  | 1新增001-004、001-005意大利高压、中压 2、新增005-002、005-003丹麦东部、西部 3、009-000、009-001英国G98、G99过频降载相关使能位修改 4、012-000波兰失能高低穿 5、030-000捷克安规修改 | 侯意
2022-11-16 |  | V2.0 |  | 1、修改罗马尼亚安规 2、修改奥地利安规 | 侯意
2022-11-10 |  | V1.9 |  | 1、028-000巴西更新至最新认证标准 | 侯意
2022-11-03 |  | V1.8 |  | 1、修改捷克常压安规 2、添加捷克中压安规 3、修改001-000开机等待时间 4、添加010-010中来安规 5、添加015-000、015-001瑞士安规（此安规测试部还未确认，如需要提前使用，在每页参数前增加国家编码15即可导出） | 侯意
2022-08-12 |  | V1.7 |  | 修改菲律宾额定电压，澳洲相关安规逻辑接口参数50549相关高低穿参数 | 侯意
2022-08-02 |  | V1.6 |  | 增加2503印度CEA安规 | 胡文浩
2022-07-15 |  | V1.5 |  | 增加2503印度CEA安规 | 胡文浩
2022-07-14 |  | V1.5 |  | 德国4105、奥地利、50549及相关安规修改（高低穿进入点修改为115%Un和80%Un） | 侯意
2022-06-29 |  | V1.4 |  | 增加123罗马尼亚安规 | 侯意
2022-06-09 |  | V1.3 |  | 删除澳大利亚多余的地区 | 李梓乐
2021-12-29 |  | V1.2 |  | 增加根据机型区分参数 | 李梓乐
2021-12-16 |  | V1.1 |  | 使能位迁移到各自表格 | 李梓乐

## 启动参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | ConnectWaitTime | PowerUpSpeed | ReconnectWaitTime | ReconnectPowerUpSpeed | VoltHighLimit | VoltLowLimit | FreqHighLimit | FreqLowLimit | ReconnectVoltHighLimit | ReconnectVoltLowLimit | ReconnectFreqHighLimit | ReconnectFreqLowLimit
[7 empty] | 并网前等待时间 | 100表示1分钟升到满载对应的速率，其他值以此为基准进行乘除计算 | 电网故障恢复后重新并网前等待时间 | 100表示1分钟升到满载对应的速率，其他值以此为基准进行乘除计算 | 启动电网电压上限 | 启动电网电压下限 | 启动电网频率上限 | 启动电网频率下限 | 重连电网电压上限 | 重连电网电压下限 | 重连电网频率上限 | 重连电网频率下限
安规版本只需要修改下面第四行 | [5 empty] | 精度（自动转换，本文档填写时请忽略） | 1 | 1 | 1 | 1 | 0.1 | 0.1 | 0.01 | 0.01 | 0.1 | 0.1 | 0.01 | 0.01
902 |  |  |  | 参数单位 |  | 单位（对应文档中的数值） | s | %Pn/min | s | %Pn/min | V | V | Hz | Hz | V | V | Hz | Hz
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | ≥60s | <10% | ≥60s | <10% | 110%(253) | 85%(195.5) | 50.1 | 47.5 | 110%(253) | 85%(195.5) | 50.1 | 47.5
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 47.5 | 253 | 195.5 | 50.1 | 47.5
[6 empty] | 旧4110标准 | 300 | 30% | 300 | 30% | 110%Un | 90%Un | 开机重连50.2HZ， | 开机重连47.5HZ | 110%Un | 95%Un | 故障重连50.1HZ | 故障重连49.9HZ
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 300 | 30 | 300 | 30 | 253 | 207 | 50.2 | 47.5 | 253 | 218.5 | 50.1 | 49.9
[6 empty] | 德国该标准已撤销 | ≥60s | <10% | ≥60s | <10% | 110%Un | 85%Un | <50.05Hz | >47.55Hz | 110%Un | 85%Un | <50.05Hz | >47.55Hz
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.05 | 47.55 | 253 | 195.5 | 50.04 | 47.6
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 300 | 30% | 300 | 30% | 110%Un | 90%Un | 开机重连50.2HZ， | 开机重连47.5HZ | 110%Un | 95%Un | 故障重连50.1HZ | 故障重连49.9HZ
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 300 | 30 | 300 | 30 | 253 | 207 | 50.2 | 47.5 | 253 | 218.5 | 50.1 | 49.9
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 300 | 30% | 300 | 30% | 110%Un | 90%Un | 开机重连50.2HZ， | 开机重连47.5HZ | 110%Un | 95%Un | 故障重连50.1HZ | 故障重连49.9HZ
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 300 | 30 | 300 | 30 | 253 | 207 | 50.2 | 47.5 | 253 | 218.5 | 50.1 | 49.9
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | ≥30s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | ≥300s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 110%Un | 85%Un | 50.1Hz | 49.9Hz | 110%Un | 85%Un | 50.1Hz | 49.9Hz
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 300 | 8 | 300 | 8 | 253 | 195.5 | 50.1 | 49.9 | 253 | 195.5 | 50.1 | 49.9
[6 empty] | 1、正标 2、系统电压≤1KV | ≥30s | ≤20% | ≥300s | ≤20% | 110%Un | 90%Un | 50.1 | 49.9 | 110%Un | 90%Un | 50.1 | 49.9
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 300 | 8 | 300 | 8 | 253 | 207 | 50.1 | 49.9 | 253 | 207 | 50.1 | 49.9
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | ≥300s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | ≥300s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 110%Un | 85%Un | 50.1 | 49.9 | 110%Un | 85%Un | 50.1 | 49.9
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 300 | 8 | 300 | 8 | 253 | 195.5 | 50.1 | 49.9 | 253 | 195.5 | 50.1 | 49.9
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | ≥300s | <10% | ≥300s | <10% | 110%Un | 85%Un | 50.1 | 49.9 | 110%Un | 85%Un | 50.1 | 49.9
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 300 | 8 | 300 | 8 | 253 | 195.5 | 50.1 | 49.9 | 253 | 195.5 | 50.1 | 49.9
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压
[7 empty] | ≥300s | <10% | ≥300s | <10% | 110%Un | 90%Un | 50.1 | 49.9 | 110%Un | 90%Un | 50.1 | 49.9
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 300 | 8 | 300 | 8 | 342 | 280 | 50.1 | 49.9 | 342 | 280 | 50.1 | 49.9
[7 empty] | ≥300s | <10% | ≥300s | <10% | 110%Un | 90%Un | 50.1 | 49.9 | 110%Un | 90%Un | 50.1 | 49.9
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 300 | 8 | 300 | 8 | 316 | 259 | 50.1 | 49.9 | 316 | 259 | 50.1 | 49.9
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 60 | 16.67 | 60 | 16.67 | 110%Un | 89.13%Un | 50.15 | 47.5 | 110%Un | 89.13%Un | 50.15 | 47.5
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 60 | 16 | 60 | 16 | 253 | 205 | 50.15 | 47.5 | 253 | 205 | 50.15 | 47.5
|  |  |  | ASNZS4777.2-2020 |  |  | ≥60s | 16.67 | ≥60s | 16.67 | 110%Un | 89.13%Un | 50.15 | 47.5 | 110%Un | 89.13%Un | 50.15 | 47.5
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 60 | 16 | 60 | 16 | 253 | 205 | 50.15 | 47.5 | 253 | 205 | 50.15 | 47.5
|  |  |  | ASNZS4777.2-2020 |  |  | 60 | 16.67 | 60 | 16.67 | 110%Un | 89.13%Un | 50.15 | 47.5 | 110%Un | 89.13%Un | 50.15 | 47.5
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 60 | 16 | 60 | 16 | 253 | 205 | 50.15 | 47.5 | 253 | 205 | 50.15 | 47.5
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | ≥180 | / | ≥180 | / | 110%Un | 85%Un | 50.5 | 48 | 110%Un | 85%Un | 50.5 | 48
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 180 | 100 | 180 | 100 | 253 | 195.5 | 50.5 | 48 | 253 | 195.5 | 50.5 | 48
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | ≥180 | / | ≥180 | / | 110%Un | 85%Un | 50.5 | 48 | 110%Un | 85%Un | 50.5 | 48
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 180 | 100 | 180 | 100 | 253 | 195.5 | 50.5 | 48 | 253 | 195.5 | 50.5 | 48
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | ≥180 | / | ≥180 | / | 110%Un | 85%Un | 50.5 | 48 | 110%Un | 85%Un | ≤50（误差±0.01） | 48
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 180 | 100 | 180 | 100 | 253 | 195.5 | 50.5 | 48 | 253 | 195.5 | 50 | 48
|  |  |  | Spain island | 西班牙island |  | ≥180 | / | ≥180 | / | 110%Un | 85%Un | 50.5 | 47.5 | 110%Un | 85%Un | 50.5 | 47.5
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 180 | 100 | 180 | 100 | 253 | 195.5 | 50.5 | 47.5 | 253 | 195.5 | 50.5 | 47.5
[6 empty] | 非标低压安规文件 | 60S | <10% | 60S | <10% | 110%Un | 85%Un | 50.1Hz | 49.9Hz | 110%Un | 85%Un | 50.1Hz | 49.9Hz
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 60 | 8 | 60 | 8 | 140 | 108 | 50.1 | 49.9 | 140 | 108 | 50.1 | 49.9
|  |  |  | EU-EN50549-1 | 土耳其 |  | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.1HZ ） | 47-50（默认47.5HZ ） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.2HZ ） | 47-50（默认47.5HZ ）
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 47.5 | 253 | 195.5 | 50.2 | 47.5
|  |  |  | EU-EN50549-1 | 丹麦 |  | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.1HZ ） | 47-50（默认47.5HZ ） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.2HZ ） | 47-50（默认47.5HZ ）
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 47.5 | 253 | 195.5 | 50.2 | 47.5
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | ≥180 | 默认<10%（可调） | ≥180 | 默认<10%（可调） | 110%Un | 85%Un | 50.1 | 49.9 | 110%Un | 85%Un | 50.1 | 49.9
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 180 | 8 | 180 | 8 | 253 | 195.5 | 50.1 | 49.9 | 253 | 195.5 | 50.1 | 49.9
|  |  |  | EU-EN50549-1 |  |  | >180s | <20%Pn/min | >180s | <20%Pn/min | 110%Un | 85%Un | 50.2 | 47.5 | 110%Un | 85%Un | 50.2 | 47.5
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 180 | 8 | 180 | 8 | 253 | 195.5 | 50.2 | 47.5 | 253 | 195.5 | 50.2 | 47.5
|  |  |  | EU-EN50549-1 |  |  | >180s | <20%Pn/min | >180s | <20%Pn/min | 110%Un | 85%Un | 50.5 | 47.5 | 110%Un | 85%Un | 50.5 | 47.5
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 180 | 8 | 180 | 8 | 253 | 195.5 | 50.5 | 47.5 | 253 | 195.5 | 50.5 | 47.5
|  |  |  | VDE0126(Greece Continent) |  |  | 10-600 | 6-3000 | 10-600 | 6-3000 | 100%-120%Un | 50%-100%Un | 50.05Hz | 47-50 | 100%-120%Un | 50%-100%Un | 50.05Hz | 47-50
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 180 | 8 | 180 | 8 | 253 | 184 | 50.05 | 47.5 | 253 | 184 | 50.05 | 47.5
|  |  |  | VDE0126(Greece island) |  |  | 10-600 | 6-3000 | 10-600 | 6-3000 | 100%-120%Un | 50%-100%Un | 50.05Hz | 47-50 | 100%-120%Un | 50%-100%Un | 50.05Hz | 47-50
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 180 | 8 | 180 | 8 | 253 | 184 | 50.05 | 47.5 | 253 | 184 | 50.05 | 47.5
|  |  |  | EU-EN50549-1 | 荷兰 |  | 10-600 | 6-3000 | 10-600 | 6-3000 | 100%-120%Un | 50%-100%Un | 50-52建议值（50.1Hz） | 48Hz | 100%-120%Un | 50%-100%Un | 50-52建议值（50.1Hz） | 48Hz
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 48 | 253 | 195.5 | 50.1 | 48
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压
|  |  |  | C10/11 | 比利时 |  | ≥60s | <10% | ≥60s | <10% | 110%Un | 85%Un | 50.1Hz | 49.9Hz | 110%Un | 85%Un | 50.1Hz | 49.9Hz
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 49.9 | 253 | 195.5 | 50.1 | 49.9
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压
[6 empty] | 非标低压安规文件 | ≥60s | <10% | ≥60s | <10% | 110%Un | 85%Un | 50.1Hz | 49.9Hz | 110%Un | 85%Un | 50.1Hz | 49.9Hz
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 60 | 8 | 60 | 8 | 140 | 108 | 50.1 | 49.9 | 140 | 108 | 50.1 | 49.9
|  |  |  | UK-G99标准 |  |  | ≥20s | / | ≥20s | / | 114%Un | 85%Un | 52 | 47.5 | 114%Un | 85%Un | 52 | 47.5
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 60 | 100 | 60 | 100 | 262.2 | 195.5 | 52 | 47.5 | 262.2 | 195.5 | 52 | 47.5
|  |  |  | UK-G98标准 |  |  | ≥20s | / | ≥20s | / | 114%Un | 85%Un | 52 | 47.5 | 114%Un | 85%Un | 52 | 47.5
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 60 | 100 | 60 | 100 | 262.2 | 195.5 | 52 | 47.5 | 262.2 | 195.5 | 52 | 47.5
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 20s-5min | <10% | 20s-5min | <10% | 110%Un | 85%Un | 50.2HZ | 49.5 | 110%Un | 85%Un | 50.2HZ | 49.5
902 | 10 | 中国 | 00 | China | 中国 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.2 | 49.5 | 253 | 195.5 | 50.2 | 49.5
|  |  |  | CNS+15382-2018 |  |  | 20s-5min | / | 20s-5min | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 300 | 100 | 300 | 100 | 242 | 187 | 61 | 59 | 242 | 187 | 61 | 59
NB/T 32004-2018
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 60 | 8 | 60 | 8 | 285 | 160 | 52 | 47 | 285 | 160 | 52 | 47
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 60 | 8 | 60 | 8 | 242 | 154 | 51.01 | 48.49 | 242 | 154 | 51.01 | 48.49
|  |  |  | NB/T 32004-2018 |  |  | 60 | 8 | 60 | 8 | 290 | 195.5 | 50.2 | 49.5 | 290 | 195.5 | 50.2 | 49.5
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 60 | 8 | 60 | 8 | 290 | 195.5 | 50.2 | 49.5 | 290 | 195.5 | 50.2 | 49.5
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 20s-5min | <10% | 20s-5min | <10% | 110%Un | 85%Un | 50.2HZ | 49.5 | 110%Un | 85%Un | 50.2HZ | 49.5
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.2 | 49.5 | 253 | 195.5 | 50.2 | 49.5
NB/T 32004-2018
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 60 | 8 | 60 | 8 | 275 | 195.5 | 50.2 | 49.5 | 275 | 195.5 | 50.2 | 49.5
902 |  | 中国 | 07 | China-MV | 中国-中压
902 |  | 中国 | 08 | China-HV | 中国-高压
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | 20s-5min | <10% | 是否自行恢复并网依据当地电网要求决定 | <10% | 110%Un | 90%Un | 50.5HZ | 48.5 | 110%Un | 90%Un | 50.5HZ | 48.5
902 | 10 | 中国 | 09 | China-A | 中国 |  | 60 | 8 | 60 | 8 | 253 | 207 | 50.5 | 48.5 | 253 | 207 | 50.5 | 48.5
[5 empty] | 中国CQC B类 |  | 20s-5min | <10% | 20s-5min | <10% | 280 | 195.5 | 50.2HZ | 49.5 | 280 | 195.5 | 50.2HZ | 49.5
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 60 | 8 | 60 | 8 | 280 | 195.5 | 50.2 | 49.5 | 280 | 195.5 | 50.2 | 49.5
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 60 | 8 | 60 | 8 | 285 | 160 | 52 | 47 | 285 | 160 | 52 | 47
[5 empty] | 中国CQC B类 |  | 60 | 8 | 60 | 8 | 286V | 85%Un | 50.2 | 49.5 | 286V | 85%Un | 50.2 | 49.5
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 60 | 8 | 60 | 8 | 286 | 195.5 | 50.2 | 49.5 | 286 | 195.5 | 50.2 | 49.5
|  |  |  | France | 法国VDE0126 | 2024年会失效 | ≧60s | ≤10% | ≧60s | ≤10% | 110%Un | 85%Un | 50.05 | 47.5 | 110%Un | 85%Un | 50.05 | 47.5
902 | 11 | 法国 | 00 | France | 法国 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
|  |  |  | FRArrete23 | 法国Arrete23 |  | / | 12.5-250W/s | / | 12.5-250W/s | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 47.5 | 253 | 195.5 | 50.1 | 47.5
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | ≧60s | ≤10% | ≧60s | ≤10% | 110%Un | 85%Un | 51.5 | 47.5 | 110%Un | 85%Un | 51.5 | 47.5
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 51.5 | 47.5 | 253 | 195.5 | 51.5 | 47.5
|  |  |  | France | 法国VDE0126 | Enedis客户 | ≧60s | ≤10% | ≧60s | ≤10% | 110%Un | 85%Un | 50.05 | 47.5 | 110%Un | 85%Un | 50.05 | 47.5
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | ≧60s | ≤10% | ≧60s | ≤10% | 110%Un | 85%Un | 51.5 | 47.5 | 110%Un | 85%Un | 51.5 | 47.5
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 51.5 | 47.5 | 253 | 195.5 | 51.5 | 47.5
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 10-600（默认60s） | 6-3000（默认100%Pn/min） | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 100%-120%Un（默认253V） | 50%-100%Un（默认195.5V） | 50-52（默认启动电网50.1HZ ） | 47-50（默认49.5Hz） | 100%-120%Un（默认253V） | 50%-100%Un（默认195.5V） | 50-52（默认启动重连50.2HZ） | 47-50（默认49.5Hz）
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 60 | 100 | 60 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 10-600（默认60s） | 6-3000（默认100%Pn/min） | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.1HZ ） | 47-50（默认49.5Hz） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动重连50.2HZ） | 47-50（默认49.5Hz）
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 60 | 100 | 60 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | ≥60 | <10% | ≥60 | <10% | 110%Un | 85%Un | 50.05 | 49 | 110%Un | 85%Un | 50.05 | 49
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.05 | 49 | 253 | 195.5 | 50.05 | 49
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | ≥60 | <10% | ≥60 | <10% | 110%Un | 85%Un | 50.05 | 49 | 110%Un | 85%Un | 50.05 | 49
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.05 | 49 | 253 | 195.5 | 50.05 | 49
|  |  |  | TOR Erzeuger Typ A | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | ≧60s | ＜10%Pn | ≧300s | ＜10%Pn | 109%Un | 85%Un | 50.1Hz | 47.5Hz | 109%Un | 85%Un | 50.1Hz | 47.5Hz
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 60 | 8 | 300 | 8 | 250.7 | 195.5 | 50.1 | 47.5 | 250.7 | 195.5 | 50.1 | 47.5
902 | 14 | 日本 | 00
|  |  |  | Switzerland Type A | 瑞士 Type A |  | 60 | 10 | 60 | 10 | 253 | 196 | 50.1 | 47.5 | 253 | 196 | 50.1 | 47.5
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 60 | 10 | 60 | 10 | 253 | 196 | 50.1 | 47.5 | 253 | 196 | 50.1 | 47.5
|  |  |  | Switzerland Type B | 瑞士 Type B |  | 600 | 10 | 600 | 10 | 253 | 196 | 50.1 | 47.5 | 253 | 196 | 50.1 | 47.5
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 600 | 10 | 600 | 10 | 253 | 196 | 50.1 | 47.5 | 253 | 196 | 50.1 | 47.5
902 | 16-17
|  |  |  | EU-EN50438 |  | 被 EN50549替代 | 60 | <10% | 60 | <10% | 253 | 195.5 | 50.1 | 47.5 | 253 | 195.5 | 50.1 | 47.5
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.1 | 47.5 | 253 | 195.5 | 50.1 | 47.5
|  |  |  | EU-EN50549-1 | 欧洲-EN50549-1 | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 10-600（默认60s） | 6-3000（默认100%Pn/min） | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.1HZ ） | 47-50（默认49.5Hz） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动重连50.2HZ） | 47-50（默认49.5Hz）
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 60 | 100 | 60 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
902 | 18 | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压
|  | 欧洲通用 |  | EU-50549-2 | 欧洲-EN50549-2 |  | 10-600（默认60s） | 6-3000（默认100%Pn/min） | 10-600（默认60s） | 6-3000（默认8%Pn/min） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动电网50.1HZ ） | 47-50（默认49.5Hz） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认85%Un） | 50-52（默认启动重连50.2HZ） | 47-50（默认49.5Hz）
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 60 | 100 | 60 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
|  |  | 00 | IEC EN61727 | 欧洲-IEC EN61727 |  | 20-300s | / | 20-300s | / | 110%Un | 85%Un | 51Hz | 49Hz | 110%Un | 85%Un | 51Hz | 49Hz
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 60 | 100 | 60 | 100 | 253 | 195.5 | 51 | 49 | 253 | 195.5 | 51 | 49
|  |  |  | / | / |  | 300 | 100 | 300 | 100 | 240 | 193 | 60.5 | 59.3 | 240 | 193 | 60.5 | 59.3
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 300 | 100 | 300 | 100 | 240 | 193 | 60.5 | 59.3 | 240 | 193 | 60.5 | 59.3
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 300 | 100 | 300 | 100 | 265 | 150 | 62 | 57 | 265 | 150 | 62 | 57
|  |  |  | EN50549-1 | / |  | ≧180s | ＜10%Pn | ≧180s | ＜10%Pn | 111%Un | 85%Un | 50.15 | 47.5 | 111%Un | 85%Un | 50.15 | 47.5
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 180 | 8 | 180 | 8 | 255.3 | 195.5 | 50.15 | 47.5 | 255.3 | 195.5 | 50.15 | 47.5
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 60 | 100 | 60 | 100 | 275 | 150 | 54.49 | 45.51 | 275 | 150 | 54.49 | 45.51
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压
902 | 23
[7 empty] | 180 | 10 | 180 | 10 | 110%Un | 80%Un | 51.5 | 47 | 110%Un | 80%Un | 51.5 | 47
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 180 | 10 | 180 | 10 | 253 | 184 | 51.5 | 47 | 253 | 184 | 51.5 | 47
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 180s | 10% | 180s | 10% | 110%Un(253) | 85%Un(195.5) | 50.05 | 47.5 | 110%Un(253) | 85%Un(195.5) | 50.05 | 47.5
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 180 | 10 | 180 | 10 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 180s | 10% | 180s | 10% | 110%Un(253) | 85%Un(195.5) | 50.05 | 47.5 | 110%Un(253) | 85%Un(195.5) | 50.05 | 47.5
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 180 | 10 | 180 | 10 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
[5 empty] | 塞浦路斯等级C | P > 120kWp | 180s | 10% | 180s | 10% | 110%Un | 90%Un | 开机重连50.2HZ， | 开机重连47.5HZ | 110%Un | 95%Un | 故障重连50.1HZ | 故障重连49.9HZ
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 180 | 10 | 180 | 10 | 253 | 207 | 50.2 | 47.5 | 253 | 218.5 | 50.1 | 49.9
|  |  |  | IEC 61727 | 印度-IEC61727 |  | 20-300s | / | 20-300s | / | 110%Un | 85%Un | 51Hz | 49Hz | 110%Un | 85%Un | 51Hz | 49Hz
902 | 25 | 印度 | 00 | India | 印度 |  | 60 | 100 | 60 | 100 | 253 | 195.5 | 51 | 49 | 253 | 195.5 | 51 | 49
902 |  | 印度 | 01 | India-MV | 印度-中压
902 |  | 印度 | 02 | India-HV | 印度-高压
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 60 | 8 | 60 | 8 | ≤110%Un | ＞90%Un | ≤50.5HZ | ＞49.5 | ≤110%Un | ＞90%Un | ≤50.5HZ | ＞49.5
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 60 | 8 | 60 | 8 | 250 | 210 | 50.4 | 49.6 | 250 | 210 | 50.4 | 49.6
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 20-300s | / | 20-300s | / | 110%Un | 85%Un | 51Hz | 49Hz | 110%Un | 85%Un | 51Hz | 49Hz
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 60 | 100 | 60 | 100 | 140 | 108 | 51 | 49 | 140 | 108 | 51 | 49
[6 empty] | Kerala地区安规参数 | 20-300s | / | 20-300s | / | 110%Un | 85%Un | 51Hz | 49Hz | 110%Un | 85%Un | 51Hz | 49Hz
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 60 | 100 | 60 | 100 | 253 | 195.5 | 51 | 49 | 253 | 195.5 | 51 | 49
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | / | / | / | / | / | / | / | / | / | / | / | /
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 600 | 100 | 600 | 100 | 250 | 180 | 65 | 55 | 250 | 180 | 65 | 55
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压
[7 empty] | 20s-5min | 无 | 20s-5min | 无 | 110%Un | 85%Un | 61Hz | 59Hz | 110%Un | 85%Un | 61Hz | 59Hz
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 60 | 100 | 60 | 100 | 140 | 108 | 61 | 59 | 140 | 108 | 61 | 59
|  |  |  | ASNZS4777.2-2020 | 澳洲 |  | 60 | 16.67 | 60 | 16.67 | 110%Un | 89.13%Un | 50.15 | 47.5 | 110%Un | 89.13%Un | 50.15 | 47.5
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 60 | 16 | 60 | 16 | 253 | 205 | 50.15 | 47.5 | 253 | 205 | 50.15 | 47.5
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 10-300s（默认值180s） | 10%-50% | 10-300s（默认值180s） | 10%-50%（默认值20%） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5）
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 180 | 20 | 180 | 20 | 242 | 198 | 60.2 | 59.5 | 242 | 198 | 60.2 | 59.5
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 10-300s（默认值180s） | 10%-50% | 10-300s（默认值180s） | 10%-50%（默认值20%） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5）
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 180 | 20 | 180 | 20 | 140 | 114 | 60.2 | 59.5 | 140 | 114 | 60.2 | 59.5
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 10-300s（默认值180s） | 10%-50% | 10-300s（默认值180s） | 10%-50%（默认值20%） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5）
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 180 | 20 | 180 | 20 | 253 | 207 | 60.2 | 59.5 | 253 | 207 | 60.2 | 59.5
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 10-300s（默认值180s） | 10%-50% | 10-300s（默认值180s） | 10%-50%（默认值20%） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5） | 105%Un-110%Un（默认值110%Un） | 88%Un-95%Un（默认90%Un） | 60.1-61（默认值60.2） | 59-59.9（默认值59.5）
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 180 | 20 | 180 | 20 | 279.4 | 228.6 | 60.2 | 59.5 | 279.4 | 228.6 | 60.2 | 59.5
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288
[5 empty] | 斯洛伐克VSD测试参数设定值 |  | 60s | 100% | 60s | 100% | 110%Un | 85%Un | 51.5Hz | 47.5Hz | 110%Un | 85%Un | 51.5Hz | 47.5Hz
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 60 | 100 | 60 | 100 | 253 | 195.5 | 51.5 | 47.5 | 253 | 195.5 | 51.5 | 47.5
[5 empty] | 斯洛伐克SSE测试参数设定值 |  | 60s | 100% | 180S | 100% | 253V | 207V | 50.2HZ | 49.8HZ | 253V | 207V | 50.2HZ | 49.8HZ
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 60 | 100 | 180 | 100 | 253 | 207 | 50.2 | 49.8 | 253 | 207 | 50.2 | 49.8
[5 empty] | 斯洛伐克ZSD测试参数设定值 |  | 60s | 100% | 900s | 100% | 253V | 207V | 50.5HZ | 49.5HZ | 253V | 207V | 50.5HZ | 49.5HZ
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 60 | 100 | 900 | 100 | 253 | 207 | 50.5 | 49.5 | 253 | 207 | 50.5 | 49.5
|  |  |  | EU-EN50549-1 | 欧洲-EN50549-1 |  | 300s | ＜10 | 300s | ＜10 | 110%Un | 85%Un | 50.05 | 47.5 | 110%Un | 85%Un | 50.05 | 47.5
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 300 | 8 | 300 | 8 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
|  | 捷克 |  | Czechia | 捷克(中压) |  | ＜300s | ＜10 | ＜300s | ＜10 | 100%-120%Un | 50%-100%Un | 50-52 | 47-50 | 100%-120%Un | 50%-100%Un | 50-52 | 47-50
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克(中压) |  | 60 | 8 | 60 | 8 | 342.1 | 264.3 | 50.1 | 49.5 | 342.1 | 264.3 | 50.1 | 49.5
|  |  |  | Czechia | 捷克<=16A系统 |  | 300s | ＜10 | 300s | ＜10 | 110%Un | 85%Un | 50.05 | 47.5 | 110%Un | 85%Un | 50.05 | 47.5
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 300 | 8 | 300 | 8 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
|  |  |  | Czechia | 捷克>16A系统 |  | 300s | ＜10 | 300s | ＜10 | 110%Un | 85%Un | 50.05 | 47.5 | 110%Un | 85%Un | 50.05 | 47.5
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 300 | 8 | 300 | 8 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 300s | ≤10%Pn/min(EGD机构建议9%) | 300s | ≤10%Pn/min(EGD机构建议9%) | 110%Un | 85%Un | 50.05 | 47.5 | 110%Un | 85%Un | 50.05 | 47.5
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 300 | 9 | 300 | 9 | 253 | 195.5 | 50.05 | 47.5 | 253 | 195.5 | 50.05 | 47.5
[7 empty] | 60 | 10% | 60 | 10% | 110%Un | 90%Un | 50.1 | 49.9 | 110%Un | 90%Un | 50.1 | 49.9
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 60 | 10 | 60 | 10 | 253 | 207 | 50.1 | 49.9 | 253 | 207 | 50.1 | 49.9
902 | 32
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 60 | 100 | 60 | 100 | 275 | 150 | 54.49 | 45.51 | 275 | 150 | 54.49 | 45.51
902 |  | 挪威 | 00 | Norway | 挪威
[5 empty] | 挪威低压测试参数设定值 | 非标低压安规文件 | 60s | 8% | 60s | 8% | 110.71%Un | 85.20%Un | 50.1Hz | 49.9Hz | 110.71%Un | 85.20%Un | 50.1Hz | 49.9Hz
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 60 | 8 | 60 | 8 | 140.6 | 108.2 | 50.1 | 49.9 | 140.6 | 108.2 | 50.1 | 49.9
[5 empty] | 墨西哥低压测试设定值 |  | 130 | 100 | 130 | 100 | 110.24%Un | 79.53%Un | 65 | 55 | 110.24%Un | 79.53%Un | 65 | 55
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 130 | 100 | 130 | 100 | 140 | 101 | 65 | 55 | 140 | 101 | 65 | 55
902 | 36-37
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 180 | 100 | 180 | 100 | 275 | 150 | 65 | 55 | 275 | 150 | 65 | 55
[6 empty] | ＞25A/16A | 10-600 | 6-3000 | ≥300s | ≤10% | 100%-120%Un | 50%-100%Un | 50-52 | 47-50 | 100%-120%Un | 50%-100%Un | 50-52 | 47-50
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 60 | 100 | 300 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 10-600 | 6-3000 | ≥300s | ≤10% | 100%-120%Un | 50%-100%Un | 50-52 | 47-50 | 100%-120%Un | 50%-100%Un | 50-52 | 47-50
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 60 | 100 | 300 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
[7 empty] | ＞60s（默认60） | ＜10%Pn | ＞60s（默认60） | ＜10%Pn | 110%Un | 85%Un | 52 | 48 | 110%Un | 85%Un | 52 | 48
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 52 | 48 | 253 | 195.5 | 52 | 48
[7 empty] | ＞60s（默认60） | ＜10%Pn | ＞60s（默认60） | ＜10%Pn | 110%Un | 85%Un | 52 | 48 | 110%Un | 85%Un | 52 | 48
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 52 | 48 | 253 | 195.5 | 52 | 48
[5 empty] | 泰国PEA安规标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 20S～5min | 默认<10%（可调） | 20S～5min | 默认<10%（可调） | 110%Un | 90%Un | 52 | 47 | 110%Un | 90%Un | 52 | 47
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 60 | 8 | 60 | 8 | 242 | 198 | 52 | 47 | 242 | 198 | 52 | 47
[5 empty] | 泰国MEA安规标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | ≥120s | 默认<10%（可调） | ≥120s | 默认<10%（可调） | 104.35%Un | 86.96%Un | 52 | 47 | 104.35%Un | 86.96%Un | 52 | 47
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 120 | 8 | 120 | 8 | 240 | 200 | 52 | 47 | 240 | 200 | 52 | 47
902 | 41
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用
902 | 43
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 60 | <10% | 60 | <10% | 110%Un | 85%Un | 50.5 | 47 | 110%Un | 85%Un | 50.5 | 47
902 | 44 | 南非 | 00 | SA | 南非 |  | 60 | 8 | 60 | 8 | 253 | 195.5 | 50.5 | 47 | 253 | 195.5 | 50.5 | 47
902 |  | 南非 | 01 | SA-HV | 南非-高压
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | ≥3 | 无 | ≥3 | 无 | 105%Un | 95%Un | 50.2Hz | 49Hz | 105%Un | 95%Un | 50.2Hz | 49Hz
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 3 | 8 | 3 | 8 | 241.5 | 218.5 | 50.2 | 49 | 241.5 | 218.5 | 50.2 | 49
902 | 45
[5 empty] | 迪拜安规标准 | 1kV以下 | ≥60s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | ≥300s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 105%Un | 95%Un | 50.1Hz | 49.9Hz | 105%Un | 95%Un | 50.1Hz | 49.9Hz
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 60 | 8 | 300 | 8 | 241.5 | 218.5 | 50.1 | 49.9 | 241.5 | 218.5 | 50.1 | 49.9
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | ≥60s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | ≥300s | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 105%Un | 95%Un | 50.1Hz | 49.9Hz | 105%Un | 95%Un | 50.1Hz | 49.9Hz
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 60 | 8 | 300 | 8 | 241.5 | 218.5 | 50.1 | 49.9 | 241.5 | 218.5 | 50.1 | 49.9
902 | 47-106
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 60 | 100% | 60 | ＜10 | 110%Un | 90%Un | 50.1Hz | 49.5HZ | 110%Un | 90%Un | 50.2HZ | 49.5HZ
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 60 | 100 | 60 | 8 | 253 | 207 | 50.1 | 49.5 | 253 | 207 | 50.2 | 49.5
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 60 | 100% | 60 | ＜10 | 110%Un | 90%Un | 50.1 | 49 | 110%Un | 90%Un | 50.1 | 49
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 60 | 100 | 60 | 8 | 253 | 207 | 50.1 | 49 | 253 | 207 | 50.1 | 49
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 60 | 100 | 60 | 8 | 255.3 | 195.5 | 50.1 | 49 | 255.3 | 195.5 | 50.1 | 49
902 | 110
[5 empty] | 哥伦比亚安规标准 |  | ≥60s | 无 | ≥60s | 无 | 110%Un | 85%Un | 61Hz | 59Hz | 110%Un | 85%Un | 61Hz | 59Hz
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 60 | 100 | 60 | 100 | 242 | 187 | 61 | 59 | 242 | 187 | 61 | 59
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 60 | 100 | 60 | 100 | 140 | 108 | 61 | 59 | 140 | 108 | 61 | 59
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | 60S | 100% | 60S | 100% | 110%Un | 85%Un | 50.2Hz | 47.5Hz | 110%Un | 85%Un | 50.2Hz | 47.5Hz
902 | 112 | 智利 | 00 | Chile | 智利 |  | 60 | 100 | 60 | 100 | 242 | 187 | 50.2 | 47.5 | 242 | 187 | 50.2 | 47.5
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 300 | 8 | 300 | 8 | 241.5 | 218.5 | 60.05 | 59.5 | 241.5 | 218.5 | 60.05 | 59.5
客户需求参考EU-EN50549
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 60 | 100 | 60 | 8 | 253 | 195.5 | 50.1 | 49.5 | 253 | 195.5 | 50.2 | 49.5
|  |  |  | 客户需求参考EU-EN50549 |  |  | ≤300s | 10%Pn | 60-600 | 10%Pn | 110%Un | 90%Un | 51 | 47.5 | 110%Un | 85%Un | 50.5 | 47.5
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 300 | 10 | 60 | 10 | 253 | 207 | 51 | 47.5 | 253 | 195.5 | 50.5 | 47.5
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 60 | 100 | 60 | 100 | 285 | 150 | 55.49 | 45.51 | 285 | 150 | 55.49 | 45.51
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 60 | 100 | 60 | 100 | 285 | 150 | 55.49 | 45.51 | 285 | 150 | 55.49 | 45.51
|  |  |  | AnnexC_EN 50549-2 |  |  | 10-600（默认60s） | 6-3000（默认100%Pn/min） | 10-600（默认60s） | 6-3000（默认100%Pn/min） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认90%Un） | 50-52（默认启动电网51HZ ） | 47-50（默认49Hz） | 100%-120%Un（默认110%Un） | 50%-100%Un（默认90%Un） | 50-52（默认启动重连51HZ） | 47-50（默认49Hz）
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 60 | 100 | 60 | 100 | 253 | 207 | 51 | 49 | 253 | 207 | 51 | 49

## 电压参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | 过压一级使能 | 过压二级使能 | 过压三级使能位 | 欠压一级使能 | 欠压二级使能 | 欠压三级使能位 | 10分钟过压使能 | Voltage Config 总使能位（自动生成） | RatedVoltage | FirstOvervoltageProtectionValue |  | SecondOvervoltageProtectionValue | SecondOvervoltageProtectionTime | ThirdOvervoltageProtectionValue | ThirdOvervoltageProtectionTime | FirstUnderVoltageProtectionValue | FirstUndervoltageProtectionTime | SecondUnderVoltageProtectionValue | SecondUndervoltageProtectionTime | ThirdUnderVoltageProtectionValue | ThirdUndervoltageProtectionTime | 10MinOvervoltageProtectionValue | FirstOvervoltageProtectionTimeHi（注:该寄存器与一级过压保护时间组合成32位寄存器使用） | SecondOvervoltageProtectionTimeHi（注:该寄存器与二级过压保护时间组合成32位寄存器使用） | ThirdOvervoltageProtectionTimeHi（注:该寄存器与三级过压保护时间组合成32位寄存器使用）
[14 empty] | Bit0：过压一级保护使能位 Bit1：过压二级保护使能位 Bit2：过压三级保护使能位 Bit3：欠压一级保护使能位 Bit4：欠压二级保护使能位 Bit5：欠压三级保护使能位 Bit6：10分钟过压保护使能位 | 额定电网电压 | 一级过压保护值 | 一级过压保护时间 | 二级过压保护值 | 二级过压保护时间 | 三级过压保护值 | 三级过压保护时间 | 一级欠压保护值 | 一级欠压保护时间 | 二级欠压保护值 | 二级欠压保护时间 | 三级欠压保护值 | 三级欠压保护时间 | 电网10分钟过压保护值 | 一级过压保护时间高位 | 二级过压保护时间高位 | 三级过压保护时间高位
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [8 empty] | 0.1 | 0.1 | 10 | 0.1 | 10 | 0.1 | 10 | 0.1 | 10 | 0.1 | 10 | 0.1 | 10 | 0.1 | 1 | 1 | 1
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [8 empty] | V | V | ms | V | ms | V | ms | V | ms | V | ms | V | ms | V
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 无 | 无 | 125%Un | ≤100ms | 无 | 无 | 80%Un | 3s→3.1s之间 | 45%Un | 300ms→400ms之间 | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5 | 60 | 287.5 | 60 | 0 | 10 | 184 | 3000 | 103.5 | 300 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 旧4110标准 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5V不使能 | 140ms不使能 | 125%Un | 100ms | 无 | 无 | 80%Un | 1s | 45%Un | 300ms | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5 | 140 | 287.5 | 100 | 0 | 10 | 184 | 1000 | 103.5 | 300 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 德国该标准已撤销 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | ≤200ms | 无 | 无 | 无 | 无 | 80%Un | ≤200ms | 无 | 无 | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 184 | 140 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压 | [23 empty] | 0 | 0 | 0
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5V不使能 | 140ms不使能 | 125%Un | 100ms | 无 | 无 | 80%Un | 1s | 45%Un | 300ms | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5 | 140 | 287.5 | 100 | 0 | 10 | 184 | 1000 | 103.5 | 300 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5V不使能 | 140ms不使能 | 125%Un | 100ms | 无 | 无 | 80%Un | 1s | 45%Un | 300ms | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5 | 140 | 287.5 | 100 | 0 | 10 | 184 | 1000 | 103.5 | 300 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 230 | 115%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 无 | 无 | 85%Un | （1500ms+1500ms*3%的误差）±20ms | 15%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 230 | 264.5 | 200 | 0 | 10 | 0 | 10 | 195.5 | 1500 | 34.5 | 200 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 1、正标 2、系统电压≤1KV | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 230 | 120%Un | （600ms+600ms*3%的误差）±20ms | 无 | 无 | 无 | 无 | 85%Un | （1500ms+1500ms*3%的误差）±20ms | 15%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 230 | 276 | 600 | 280 | 100 | 0 | 10 | 195.5 | 1500 | 34.5 | 200 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 无 | 0 | 0 | 0
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 253 | 900 | 264.5 | 200 | 0 | 10 | 195.5 | 900 | 34.5 | 200 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 230 | 115%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 无 | 无 | 85%Un | （1500ms+1500ms*3%的误差）±20ms | 15%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 110%Un | 0 | 0 | 0
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 230 | 264.5 | 200 | 0 | 10 | 0 | 10 | 195.5 | 1500 | 34.5 | 200 | 0 | 10 | 253 | 0 | 0 | 0
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压
[7 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 311 | 120%Un | （600ms+600ms*3%的误差）±20ms | 无 | 无 | 无 | 无 | 85%Un | （1500ms+1500ms*3%的误差）±20ms | 15%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 120%Un | 0 | 0 | 0
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 311 | 373 | 600 | 373 | 580 | 0 | 10 | 264 | 1500 | 47 | 200 | 0 | 10 | 373 | 0 | 0 | 0
[7 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 288 | 120%Un | （600ms+600ms*3%的误差）±20ms | 346 | 无 | 无 | 无 | 85%Un | （1500ms+1500ms*3%的误差）±20ms | 15%Un | （200ms+200ms*3%的误差）±20ms | 无 | 无 | 120%Un | 0 | 0 | 0
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 89 | 288 | 346 | 600 | 346 | 580 | 0 | 10 | 245 | 1500 | 43 | 200 | 0 | 10 | 346 | 0 | 0 | 0
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 115.22%Un | 1000-2000 | 119.57%Un | ≤200 | 0 | 0 | 78.26%Un | 10000-11000 | 30.43%Un | 1000-2000 | 0 | 0 | 112.17%Un | 0 | 0 | 0
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 265 | 1200 | 275 | 140 | 0 | 10 | 180 | 10500 | 70 | 1200 | 0 | 10 | 258 | 0 | 0 | 0
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 115.22%Un | 1000-2000 | 119.57%Un | ≤200 | 0 | 0 | 78.26%Un | 10000-11000 | 30.43%Un | 1000-2000 | 0 | 0 | 112.17%Un | 0 | 0 | 0
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 265 | 1200 | 275 | 140 | 0 | 10 | 180 | 10500 | 70 | 1200 | 0 | 10 | 258 | 0 | 0 | 0
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 115.22%Un | 1000-2000 | 119.57%Un | ≤200 | 0 | 0 | 78.26%Un | 10000-11000 | 30.43%Un | 1000-2000 | 0 | 0 | 112.17%Un | 0 | 0 | 0
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 265 | 1200 | 275 | 140 | 0 | 10 | 180 | 10500 | 70 | 1200 | 0 | 10 | 258 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压 | [23 empty] | 0 | 0 | 0
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 110%Un | ≤1500 | 115%Un | ≤200 | 0 | 0 | 85%Un | ≤1500 | / | / | / | 0 | / | 0 | 0 | 0
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 253 | 1400 | 264.5 | 160 | 0 | 10 | 195.5 | 1400 | 175 | 160 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 110%Un | ≤1500 | 115%Un | ≤200 | 0 | 0 | 85%Un | ≤1500 | / | / | / | 0 | / | 0 | 0 | 0
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 253 | 1400 | 264.5 | 160 | 0 | 10 | 195.5 | 1400 | 175 | 160 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 110%Un | ≤1500 | 115%Un | ≤200 | 0 | 0 | 85%Un | ≤1500 | / | / | / | 0 | / | 0 | 0 | 0
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 253 | 1400 | 264.5 | 160 | 0 | 10 | 195.5 | 1200 | 175 | 160 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | Spain island | 西班牙island |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 110%Un | ≤1500 | 115%Un | ≤200 | 0 | 0 | 85%Un | ≤1500 | / | / | / | 0 | / | 0 | 0 | 0
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 253 | 1400 | 264.5 | 160 | 0 | 10 | 195.5 | 1400 | 175 | 160 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 非标低压安规文件 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 127V | 110%Un | ≤1500 | 115%Un | ≤200 |  |  | 85%Un | ≤1500
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 127 | 140 | 1400 | 146 | 160 | 0 | 10 | 108 | 1400 | 175 | 160 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 | 土耳其 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 1.0Un-1.2Un | 100-100000 | 1.0Un-1.3Un | 100-5000 | 0 | 0 | 0.2Un-1.0Un | 100-100000 | 0.2Un-1.0Un | 100-5000 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 20 | 0 | 10 | 195.5 | 1400 | 115 | 20 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 | 丹麦 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 110%Un | 39000-40000 | 113%Un | 100-200 | 0 | 0 | 90%Un | 9000-10000 | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 253 | 39000 | 259.9 | 100 | 0 | 10 | 207 | 9000 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 110%Un | 默认值60-60.1S | 115%Un | 默认值200-300ms | / | / | 85%Un | （可调值10-60S，默认值50-50.1S） | 80%Un | 可调值50-1500ms，默认值100-200ms | / | / | / | 0 | 0 | 0
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 253 | 60000 | 264.5 | 200 | 0 | 10 | 195.5 | 50000 | 184 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 100%UnUn-120%Un（默认110%Un） | 100-100000（默认60000） | 100%Un-130%Un（默认115%Un） | 100-5000（默认200） | 0 | 0 | 20%Un-100%Un（默认85%Un） | 100-100000（默认50000） | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 253 | 60000 | 264.5 | 200 | 0 | 10 | 195.5 | 50000 | 0 | 10 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 100%UnUn-120%Un（默认110%Un） | 100-100000（默认60000） | 100%Un-130%Un（默认115%Un） | 100-5000（默认200） | 0 | 0 | 20%Un-100%Un（默认85%Un） | 100-100000（默认50000） | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 253 | 60000 | 264.5 | 200 | 0 | 10 | 195.5 | 50000 | 0 | 10 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | VDE0126(Greece Continent) |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un（264.5） | ≤500ms | 0 | 0 | 0 | 0 | 80%Un（184） | ≤500ms | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 400 | 273 | 20 | 0 | 10 | 184 | 400 | 115 | 20 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | VDE0126(Greece island) |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un（264.5） | ≤500ms | 0 | 0 | 0 | 0 | 80%Un（184） | ≤500ms | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 400 | 273 | 20 | 0 | 10 | 184 | 400 | 115 | 20 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 | 荷兰 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 1.1Un | ≤2000 | 0 | 0 | 0 | 0 | 0.8Un | ≤2000 | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 253 | 1400 | 273 | 60 | 0 | 10 | 184 | 1400 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | C10/11 | 比利时 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 1.15Un | ≤200 | 0 | 0 | 0 | 0 | 0.8Un | ≤200 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 20 | 0 | 10 | 184 | 140 | 175 | 20 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压 | [23 empty] | 0 | 0 | 0
[6 empty] | 非标低压安规文件 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 127 | 1.15Un | ≤200 | 0 | 0 | 0 | 0 | 0.8Un | ≤200 | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 127 | 146 | 140 | 0 | 10 | 0 | 10 | 101.6 | 140 | 0 | 10 | 0 | 10 | 140 | 0 | 0 | 0
|  |  |  | UK-G99标准 |  |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 114%Un | 1000 | 119%Un | 500 | / | / | 80%Un | 2500-3000 | / | / | / | / | / | 0 | 0 | 0
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 262.2 | 1000 | 273.7 | 500 | 0 | 10 | 184 | 2500 | 0 | 10 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | UK-G98标准 |  |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 114%Un | 1000 | 119%Un | 500 | / | / | 80%Un | 2500-3000 | / | / | / | / | / | 0 | 0 | 0
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 262.2 | 1000 | 273.7 | 500 | 0 | 10 | 184 | 2500 | 0 | 10 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 110%Un≤U＜135%Un | ≤2s | 135%Un≤U | ≤0.2s | / | / | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤0.2s | / | / | / | 0 | 0 | 0
902 | 10 | 中国 | 00 | China | 中国 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 1500 | 282 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | CNS+15382-2018 |  |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 220 | 110%Un＜U≤135%Un | ≤2s | 135%Un＜U | ≤0.05s | / | / | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤0.1s | 0 | / | 0 | 0 | 0 | 0
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 220 | 242 | 1900 | 297 | 20 | 0 | 10 | 187 | 1900 | 110 | 50 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | NB/T 32004-2018 | [24 empty] | 0 | 0 | 0
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 285 | 1500 | 295 | 20 | 0 | 10 | 160 | 1500 | 110 | 40 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 220 | 242 | 1900 | 264 | 100 | 0 | 10 | 154 | 1900 | 99 | 100 | 0 | 10 | 253 | 0 | 0 | 0
[7 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 230 | 290 | 1500 | 282 | 20 | 0 | 0 | 195.5 | 1500 | 118 | 40 | 0 | 0 | 253 | 0 | 0 | 0
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 230 | 290 | 1500 | 282 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 110%Un≤U＜135%Un | ≤2s | 135%Un≤U | ≤0.2s | / | / | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤0.2s | / | / | / | 0 | 0 | 0
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 1500 | 282 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | NB/T 32004-2018 | [11 empty] | 110%Un≤U＜135%Un | ≤2s | [11 empty] | 0 | 0 | 0
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 275 | 1500 | 282 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 中国 | 07 | China-MV | 中国-中压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 中国 | 08 | China-HV | 中国-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 无 | 无 | 无 | 无 | / | / | 无 | 无 | 无 | 无 | / | / | / | 0 | 0 | 0
902 | 10 | 中国 | 09 | China | 中国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 253 | 1500 | 282 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 中国CQC B类 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 110%Un≤U＜135%Un | ≤2s | 135%Un≤U | ≤0.2s | / | / | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤0.2s | / | / | / | 0 | 0 | 0
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 280 | 1500 | 282 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 285 | 1500 | 295 | 20 | 0 | 10 | 160 | 1500 | 110 | 40 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 中国CQC B类 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 286V | ≤2s | 295V | ≤0.2s | / | / | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤0.2s | / | / | / | 0 | 0 | 0
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 286 | 1500 | 295 | 20 | 0 | 10 | 195.5 | 1500 | 118 | 40 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | ≤0.2s | / | / | / | / | 80%Un | ≤0.2s | / | / | / | / | 110%Un | 0 | 0 | 0
902 | 11 | 法国 | 00 | France | 法国 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 184 | 140 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | FRArrete23 | 法国Arrete23 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 35%Un-195%Un | 0.01s-200s | 35%Un-195%Un | 0.01s-200s | 0 | 0 | 35%Un-195%Un | 0.01s-200s | 35%Un-195%Un | 0.01s-200s | 0 | 0 | 0 | 0 | 0 | 0
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 184 | 140 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压 | [23 empty] | 0 | 0
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | ≤0.2s | / | / | / | / | 80%Un | ≤0.2s | / | / | / | / | 110%Un | 0 | 0 | 0
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 184 | 140 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | France | 法国VDE0126 | Enedis客户 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | ≤0.2s | / | / | / | / | 80%Un | ≤0.2s | / | / | / | / | 110%Un | 0 | 0 | 0
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 184 | 140 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | ≤0.2s | / | / | / | / | 80%Un | ≤0.2s | / | / | / | / | 110%Un | 0 | 0 | 0
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 184 | 140 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 1.0Un-1.2Un（建议值264.5V） | 100-100000(建议值140ms) | 1.0Un-1.3Un | 100-5000（建议值100） | 0 | 0 | 0.2Un-1.0Un（建议值195.5） | 100-100000(建议值1.2s) | 0.2Un-1.0Un | 100-5000 | 0 | 0 | 253 | 0 | 0 | 0
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 140 | 273 | 100 | 0 | 10 | 195.5 | 1200 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 1.0Un-1.2Un（建议值1.15Un） | 100-100000(建议值140ms) | 1.0Un-1.3Un | 100-5000（建议值100） | 0 | 0 | 0.2Un-1.0Un（建议值85%Un） | 100-100000(建议值1.2s) | 0.2Un-1.0Un | 100-5000 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 140 | 273 | 100 | 0 | 10 | 195.5 | 1200 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | 100ms-200ms | 0 | 0 | 0 | 0 | 85%Un | 1200-1500 | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 180 | 270 | 120 | 0 | 10 | 195.5 | 1400 | 115 | 20 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 115%Un | 100ms-200ms | 0 | 0 | 0 | 0 | 85%Un | 1200-1500 | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 180 | 270 | 120 | 0 | 10 | 195.5 | 1200 | 0 | 10 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 |  |  | 115%Un | <=100ms |  |  | 80%Un | <=1500ms | 25%Un | <=500ms |  |  | 111%Un | 0 | 0 | 0
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 90 | 230 | 264.5 | 140 | 264.5 | 80 | 0 | 10 | 184 | 1450 | 57.5 | 450 | 0 | 10 | 255.3 | 0 | 0 | 0
902 | 14 | 日本 | 00 | [10 empty] | 0 | [14 empty] | 0 | 0 | 0
|  |  |  | Switzerland Type A | 瑞士 Type A |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 60 | 276 | 40 | 0 | 0 | 184 | 1450 | 104 | 250 | 0 | 0 | 253 | 0 | 0 | 0
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 60 | 276 | 40 | 0 | 10 | 184 | 1450 | 104 | 250 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | Switzerland Type B | 瑞士 Type B |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 60 | 276 | 40 | 0 | 0 | 184 | 1450 | 104 | 250 | 0 | 0 | 253 | 0 | 0 | 0
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 60 | 276 | 40 | 0 | 10 | 184 | 1450 | 104 | 250 | 0 | 10 | 253 | 0 | 0 | 0
902 | 16-17 | [12 empty] | 0 | [14 empty] | 0 | 0 | 0
|  |  |  | EU-EN50438 |  | 被 EN50549替代 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 100ms-200ms | 0 | 0 | 0 | 0 | 195.5 | 1200-1500 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 140 | 273 | 60 | 0 | 10 | 195.5 | 1200 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 欧洲-EN50549 | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 1.0Un-1.2Un（建议值1.15Un） | 100-100000(建议值140ms) | 1.0Un-1.3Un | 100-5000（建议值100） | 0 | 0 | 0.2Un-1.0Un（建议值0.85Un） | 100-100000(建议值1.2s) | 0.2Un-1.0Un | 100-5000 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 140 | 273 | 100 | 0 | 10 | 195.5 | 1200 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压 | [23 empty] | 0 | 0 | 0
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 1.0Un-1.2Un（建议值1.15Un） | 100-100000(建议值140ms) | 1.0Un-1.3Un | 100-5000（建议值100） | 0 | 0 | 0.2Un-1.0Un（建议值85%Un） | 100-100000(建议值1.2s) | 0.2Un-1.0Un | 100-5000 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 140 | 273 | 100 | 0 | 10 | 195.5 | 1200 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  | IEC EN61727 | 00 | IEC EN61727 | 欧洲-IEC EN61727 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 110%Un | ≤2s | 135%Un | ≤0.05s | 0 | 0 | 85%Un | ≤2s | 50%Un | ≤0.1s | 0 | 0 | / | 0 | 0 | 0
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 1600 | 310.5 | 20 | 0 | 10 | 195.5 | 1600 | 115 | 20 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 |  |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 220 | 110%Un＜U＜120%Un | 200-1000 | U≥120%Un | 0-160 | / | / | 70%Un≤V<90%Un | 1500-2000 | 50%Un≤V<70%Un | 160-2000 | V<50%Un | 150-500 | / | 0 | 0 | 0
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 220 | 243 | 300 | 263 | 40 | 0 | 10 | 197 | 1800 | 153 | 1000 | 109 | 200 | 253 | 0 | 0 | 0
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 220 | 242 | 300 | 264 | 80 | 0 | 10 | 198 | 1800 | 154 | 300 | 110 | 200 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 |  |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 230 | 111%Un | 6000 | 86.96%Un | 200 | 0 | 0 | 85%Un | 200 | 0 | 0 | 0 | 0 | 无 | 0 | 0 | 0
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 255.3 | 60000 | 264.5 | 200 | 0 | 10 | 195.5 | 200 | 175 | 60 | 0 | 10 | 253 | 0 | 0 | 0
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 283 | 140 | 285 | 60 | 0 | 10 | 150 | 140 | 110 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压 | [23 empty] | 0 | 0 | 0
902 | 23 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | 0
[7 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 230 | 110%Un | 200 | 118.70%Un | 60 | 0 | 0 | 80%Un | 200 | 132.95%Un | 60 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 230 | 253 | 200 | 273 | 60 | 0 | 10 | 184 | 200 | 173 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 1 | 0 | 0 | 1 | 0 | 0 | 1 |  | 230 | 110%Un | 200ms | / | / | / | / | 80%Un | 200ms | / | / | / | / | 110%Un
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 253 | 200 | 273 | 60 | 0 | 10 | 184 | 200 | 173 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 0 | 0 | 1 | 0 | 0 | 1 |  | 230 | 115%Un | 200ms | / | / | / | / | 90%Un | 1500ms | / | / | / | / | 110%Un
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 200 | 273 | 60 | 0 | 10 | 207 | 1500 | 173 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 0 | 0 | 1 | 0 | 0 | 1 |  | 230 | 115%Un | 200ms | / | / | / | / | 90%Un | 1500ms | / | / | / | / | 110%Un
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 73 | 230 | 264.5 | 200 | 273 | 60 | 0 | 10 | 207 | 1500 | 173 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | IEC61727 | 印度-IEC61727 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 110%Un | ≤2s | 135%Un | ≤0.05s | 0 | 0 | 85%Un | ≤2s | 50%Un | ≤0.1s | 0 | 0 | / | 0 | 0 | 0
902 | 25 | 印度 | 00 | India | 印度 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 1900 | 310.5 | 20 | 0 | 10 | 195.5 | 1900 | 115 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 印度 | 01 | India-MV | 印度-中压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 印度 | 02 | India-HV | 印度-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 230 | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | 0 | 0
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 253 | 1900 | 280 | 20 | 0 | 10 | 195.5 | 1900 | 115 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 127 | 110%Un | ≤2s | 135%Un | ≤0.05s | 0 | 0 | 85%Un | ≤2s | 50%Un | ≤0.1s | 0 | 0 | / | 0 | 0 | 0
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 127 | 140 | 1900 | 171.4 | 20 | 0 | 10 | 108 | 1900 | 63 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | Kerala地区安规参数 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 230 | 114.78%Un | ≤200ms | / | / | 0 | 0 | 83.48%Un | ≤200ms | / | / | 0 | 0 | / | 0 | 0 | 0
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 230 | 264 | 180 | 310.5 | 20 | 0 | 10 | 192 | 180 | 115 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[6 empty] | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | [22 empty] | 0 | 0 | 0
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 220 | 250 | 1900 | 280 | 60 | 0 | 10 | 180 | 1900 | 170 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压 | [23 empty] | 0 | 0 | 0
[7 empty] | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 127 | 110%Un≤U＜135%Un | ≤2s | 135%Un≤U | ≤0.05s | / | / | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤100ms | / | / | 无 | 0 | 0 | 0
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 127 | 140 | 1900 | 171.4 | 20 | 0 | 10 | 108 | 1900 | 63 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  | 00 | ASNZS4777.2-2020 | 澳大利亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 115.22%Un | 1000-2000 | 119.57%Un | ≤200 | 0 | 0 | 78.26%Un | 10000-11000 | 30.43%Un | 1000-2000 | 0 | 0 | 108.26%Un | 0 | 0 | 0
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 265 | 1200 | 275 | 140 | 0 | 10 | 180 | 10500 | 70 | 1200 | 0 | 10 | 249 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压 | [23 empty] | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 220 | 112%-118%Un（默认112%Un） | 1-1.5s（默认1s） | 118%Un≤U（默认118%Un） | 0.02s | / | / | 50%Un-80%Un（默认80%Un） | 2.5-3s（默认值2.5s） | 20%Un-50%Un（默认值50%Un） | 0.5-1s（默认值0.5s） | 0%-20%Un（默认值20%Un） | 0.02-2s（默认20ms） | / | 0 | 0 | 0
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 220 | 246.4 | 1000 | 259.6 | 20 | 0 | 10 | 176 | 2500 | 110 | 500 | 44 | 20 | 253 | 0 | 0 | 0
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 127 | 112%-118%Un（默认112%Un） | 1-1.5s（默认1s） | 118%Un≤U（默认118%Un） | 0.02s | / | / | 50%Un-80%Un（默认80%Un） | 2.5-3s（默认值2.5s） | 20%Un-50%Un（默认值50%Un） | 0.5-1s（默认值0.5s） | 0%-20%Un（默认值20%Un） | 0.02-2s（默认20ms） | 无 | 0 | 0 | 0
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 127 | 142 | 1000 | 150 | 20 | 0 | 10 | 101.6 | 2500 | 63.5 | 500 | 25.4 | 20 | 253 | 0 | 0 | 0
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 230 | 112%-118%Un（默认112%Un） | 1-1.5s（默认1s） | 118%Un≤U（默认118%Un） | 0.02s | / | / | 50%Un-80%Un（默认80%Un） | 2.5-3s（默认值2.5s） | 20%Un-50%Un（默认值50%Un） | 0.5-1s（默认值0.5s） | 0%-20%Un（默认值20%Un） | 0.02-2s（默认20ms） | 无 | 0 | 0 | 0
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 230 | 257.6 | 1000 | 271.4 | 20 | 0 | 10 | 184 | 2500 | 115 | 500 | 46 | 20 | 253 | 0 | 0 | 0
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 254 | 112%-118%Un（默认112%Un） | 1-1.5s（默认1s） | 118%Un≤U（默认118%Un） | 0.02s | / | / | 50%Un-80%Un（默认80%Un） | 2.5-3s（默认值2.5s） | 20%Un-50%Un（默认值50%Un） | 0.5-1s（默认值0.5s） | 0%-20%Un（默认值20%Un） | 0.02-2s（默认20ms） | 无 | 0 | 0 | 0
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 59 | 254 | 284.5 | 1000 | 299.7 | 20 | 0 | 10 | 203.2 | 2500 | 127 | 500 | 50.8 | 20 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288 | [23 empty] | 0 | 0 | 0
[5 empty] | 斯洛伐克VSD测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 230 | 110%Un | 80ms | 115.22%Un | 60ms |  |  | 85%Un | 80ms | 65.22%Un | 60ms |  |  | / | 0 | 0 | 0
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 80 | 265 | 60 | 0 | 10 | 195.5 | 80 | 150 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 斯洛伐克SSE测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 230 | 253V | 80ms | 265V | 60ms |  |  | 207V | 80ms | 150V | 60ms |  |  | / | 0 | 0 | 0
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 80 | 265 | 60 | 0 | 10 | 207 | 80 | 150 | 60 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 230 | 253V | 180ms | 265V | 100ms |  |  | 207V | 180ms | 150V | 100ms |  |  | / | 0 | 0 | 0
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 180 | 265 | 100 | 0 | 10 | 207 | 180 | 150 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 | 欧洲-EN50549 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 115%Un | ≤200ms | 120%Un | ＜100 | 0 | 0 | 85%Un | ≤1500ms | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 264.5 | 180 | 276 | 60 | 0 | 10 | 195.5 | 1000 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  | 捷克 |  | Czechia | 捷克（中压） |  | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 95 | 311 | 100%Un-120%Un(建议值115%Un) | ≤60s | 100%Un-130%Un（建议值120%Un） | 5000 | 100%Un-130%Un（建议值125%Un） | 100 | 20%Un-100%Un建议值（70%Un） | 1500 | 20%Un-100%Un（建议值45%Un） | ≥150 | 0 | 0 | 115%Un | 0 | 0 | 0
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 95 | 311 | 357.6 | 59000 | 373.2 | 5000 | 388.7 | 100 | 217.7 | 1500 | 139.9 | 150 | 0 | 10 | 357.6 | 0 | 0 | 0
|  |  |  | Czechia | 捷克<=16A系统 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 |  | 230 | 115%Un | 1000ms | 120%Un | 100ms | 0 | 0 | 85%Un | 1500ms | 0 | 0 | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 264.5 | 800 | 276 | 80 | 0 | 10 | 195.5 | 1350 | 0 | 10 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | Czechia | 捷克>16A系统 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 230 | 120%Un | 5000ms | 125%Un | 100ms | 0 | 0 | 70%Un | 0-2700ms | 45%Un | ≥150ms | 0 | 0 | 110%Un | 0 | 0 | 0
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 276 | 4800 | 287.5 | 80 | 0 | 10 | 161 | 1500 | 103.5 | 150 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 230 | 264.5 | 5000ms | 276 | 100ms | 0 | 0 | 70%Un | 2700ms | 45%Un | 200ms | 0 | 0 | 111%Un | 0 | 0 | 0
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 5000 | 276 | 100 | 0 | 10 | 161 | 2700 | 103.5 | 200 | 0 | 10 | 255.3 | 0 | 0 | 0
[7 empty] | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 230V | 111%Un | 2000ms | 115%Un | 200ms | / | / | 85%Un | 2000ms | 70%Un | 200ms | / | / | 110%Un | 0 | 0 | 0
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 255.3 | 2000 | 264.5 | 200 | 0 | 10 | 195.5 | 2000 | 161 | 200 | 0 | 10 | 253 | 0 | 0 | 0
902 | 32 | [27 empty] | 0 | 0 | 0
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 283 | 140 | 285 | 60 | 0 | 10 | 150 | 140 | 110 | 60 | 0 | 10 | 253 | 0 | 0 | 0
902 |  | 挪威 | 00 | Norway | 挪威 |  |  |  | 0 |  |  | 0 |  | 0 | [14 empty] | 0 | 0 | 0
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 127V | 112.28%Un | 3s | 120.24%Un | 0.1s | / | / | 83.62%Un | 1.5s | 81.50%Un | 300ms | / | / | / | 0 | 0 | 0
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 127 | 142.6 | 3000 | 152.7 | 100 | 0 | 10 | 106.2 | 1500 | 103.5 | 300 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 墨西哥低压测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 127 | 110.24%Un | 200ms | 133.07%Un | 60ms | / | / | 79.53%Un | 2s | 70.87%Un | 60ms | / | / | / | 0 | 0 | 0
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 127 | 140 | 200 | 169 | 60 | 0 | 10 | 101 | 2000 | 90 | 60 | 0 | 10 | 253 | 0 | 0 | 0
902 | 36-37 | [27 empty] | 0 | 0 | 0
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 220 | 283 | 140 | 285 | 60 | 0 | 10 | 150 | 140 | 110 | 60 | 0 | 10 | 264 | 0 | 0 | 0
[6 empty] | ＞25A/16A | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 230 | 117%Un | ≤70s | 122.2%Un | ≤0.7s | / | / | 83%Un | ≤3S | 12.6%Un | ≤0.5s | / | / | 112%Un | 0 | 0 | 0
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 269 | 65000 | 281 | 650 | 0 | 10 | 191 | 2500 | 29 | 450 | 0 | 10 | 257.6 | 0 | 0 | 0
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 1 | 1 | 0 | 1 | 0 | 0 | 1 |  | 230 | 117%Un | ≤70s | 122.2%Un | ≤0.7s | / | / | 83%Un | ≤0.7S | / | / | / | / | 110%Un | 0 | 0 | 0
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 75 | 230 | 269 | 65000 | 281 | 650 | 0 | 10 | 191 | 650 | 29 | 450 | 0 | 10 | 253 | 0 | 0 | 0
[7 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 230 | 110%Un | 500 | 119%Un | 500 | / | / | 85%Un | 3000 | 60%Un | 2000 | / | / | 253 | 0 | 0 | 0
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 230 | 253 | 500 | 273.7 | 500 | 0 | 10 | 195.5 | 3000 | 138 | 2000 | 0 | 10 | 253 | 0 | 0 | 0
[7 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 230 | 110%Un | 500 | 119%Un | 500 | / | / | 85%Un | 3000 | 60%Un | 2000 | / | / | 253 | 0 | 0 | 0
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 230 | 253 | 500 | 273.7 | 500 | 0 | 10 | 195.5 | 3000 | 138 | 2000 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 泰国PEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 220 | 110%Un | ≤1S | 120%Un | ≤0.16S | / | / | 90%Un | ≤2S | 50%Un | ≤0.3S | / | / | 无 | 0 | 0 | 0
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 220 | 242 | 600 | 264 | 60 | 0 | 10 | 198 | 1600 | 110 | 150 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 泰国MEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 230 | 104.35%Un<U<135.22%Un | ≤2S | U≧135.22%Un | ≤50ms | / | / | 50%Un≤U<86.96%Un | ≤2S | U<50%Un | ≤100ms | / | / | 无 | 0 | 0 | 0
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 241 | 1600 | 311 | 20 | 0 | 10 | 199 | 1600 | 114 | 60 | 0 | 10 | 253 | 0 | 0 | 0
902 | 41 | [27 empty] | 0 | 0 | 0
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  |  |  | 0 |  |  | 0 |  | 0 | [14 empty] | 0 | 0 | 0
902 | 43 | [27 empty] | 0 | 0 | 0
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 1 | 1 | 1 | 1 | 1 | 0 | 0 |  | 230 | 110%Un＜U＜115%Un | ≤40s | 115%Un≤U＜120%Un | ≤2s | ≥120%Un | ≤0.16S | 50%Un≤U＜85%Un | ≤10s | ＜50%Un | ≤0.2S | 0 | 0 | 无 | 0 | 0 | 0
902 | 44 | 南非 | 00 | SA | 南非 |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 31 | 230 | 253 | 1800 | 264.5 | 60 | 276 | 50 | 195.5 | 9000 | 115 | 100 | 0 | 10 | 253 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0
902 |  | 南非 | 01 | SA-HV | 南非-高压 | [23 empty] | 0 | 0 | 0
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 31 | 230 | 253 | 1800 | 264.5 | 60 | 276 | 50 | 195.5 | 9000 | 115 | 100 | 0 | 10 | 253 | 0 | 0 | 0
902 | 45 | [18 empty] | 0 | 0 | [7 empty] | 0 | 0 | 0
[5 empty] | 迪拜安规标准 | 1kV以下 | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 230 | 110%Un | 90s±20ms | 115%Un | 0.2s±20ms |  |  | 85%Un | 0.4s±20ms | 40%Un | 0.2s±20ms |  |  | 110%Un/603s | 0 | 0 | 0
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 253 | 89980 | 264.5 | 180 | 0 | 10 | 195.5 | 380 | 92 | 180 | 0 | 10 | 253 | 0 | 0 | 0
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 1 | 1 | 0 | 1 | 1 | 0 | 1 |  | 230 | 110%Un | 90S | 120%Un | 0.6s |  |  | 85%Un | 1.5S | 30%Un | 0.2s |  |  | 110%Un/603s | 0 | 0 | 0
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 253 | 90000 | 276 | 600 | 0 | 10 | 195.5 | 1500 | 69 | 200 | 0 | 10 | 253 | 0 | 0 | 0
902 | 47-106 | [27 empty] | 0 | 0 | 0
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 230 | >110%Un | 30s | >115%Un | 0.20s |  |  | <90%Un | 1.50s | <80%Un | 0.20s |  |  | / | 0 | 0 | 0
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 253 | 30000 | 264.5 | 200 | 0 | 10 | 207 | 1500 | 184 | 200 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 230 | 110%Un | 600s | 115%Un | 0.2 s |  |  | 84%Un | 600s | 80%Un | 0.2 s |  |  | / | 0 | 0 | 0
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 255.3 | 600000 | 264.5 | 200 | 0 | 10 | 193.2 | 600000 | 184 | 200 | 0 | 10 | 253 | 0 | 0 | 0
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 255.3 | 3000 | 264.5 | 100 | 0 | 10 | 195.5 | 1500 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
902 | 110 | [12 empty] | 0 | [14 empty] | 0 | 0 | 0
[5 empty] | 哥伦比亚安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 |  | 220 | 110%Un≤U＜135%Un | ≤2s | 135%Un≤U | ≤0.05s |  |  | 50%Un≤U＜85%Un | ≤2s | U＜50%Un | ≤100ms |  |  | / | 0 | 0 | 0
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 220 | 242 | 1900 | 297 | 20 | 0 | 10 | 187 | 1900 | 110 | 60 | 0 | 10 | 127 | 0 | 0 | 0
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 127 | 140 | 1900 | 170 | 20 | 0 | 10 | 108 | 1900 | 63 | 60 | 0 | 10 | 127 | 0 | 0 | 0
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | 1 | 1 | 0 | 1 | 0 | 0 | 0 |  | 220 | 110%Un | 100ms(默认80ms） | 115%Un | 100ms(默认80ms） |  |  | 80%Un | 100ms(默认80ms）
902 | 112 | 智利 | 00 | Chile | 智利 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 220 | 242 | 80 | 253 | 80 | 0 | 10 | 176 | 80 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 230 | 264.5 | 5000 | 264.5 | 60 | 0 | 10 | 195.5 | 5000 | 184 | 60 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | 客户需求参考EU-EN50549 | [24 empty] | 0 | 0 | 0
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 255 | 1500 | 273 | 100 | 0 | 10 | 195.5 | 3000 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | 客户需求参考EU-EN50549 | [11 empty] | 115%Un |  | 118.686%Un |  |  |  | 85%Un |  | 76.087%Un |  |  |  | 110%Un | 0 | 0 | 0
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 500 | 273 | 100 | 0 | 10 | 195.5 | 3200 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 285 | 140 | 287 | 60 | 0 | 0 | 150 | 140 | 110 | 60 | 0 | 0 | 265 | 0 | 0 | 0
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 285 | 140 | 287 | 60 | 0 | 10 | 150 | 140 | 110 | 60 | 0 | 10 | 265 | 0 | 0 | 0
|  |  |  | AnnexC_EN 50549-2 |  |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 1.0Un-1.2Un（建议值1.15Un） | 100-100000(建议值140ms) | 1.0Un-1.3Un | 100-5000（建议值100） | 0 | 0 | 0.2Un-1.0Un（建议值0.85Un） | 100-100000(建议值1.2s) | 0.2Un-1.0Un | 100-5000 | 0 | 0 | 100%Un-115%Un（默认110%Un） | 0 | 0 | 0
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 91 | 230 | 264.5 | 140 | 273 | 100 | 0 | 10 | 195.5 | 1200 | 175 | 100 | 0 | 10 | 253 | 0 | 0 | 0

## 频率参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | 过频一级保护使能位 | 过频二级保护使能位 | 过频三级保护使能位 | 欠频一级保护使能位 | 欠频二级保护使能位 | 欠频三级保护使能位 | 频率变化率保护使能位 | FrequencyConfig总使能位（自动生成) | RatedFrequency | FirstOverfrequencyProtectionValue | FirstOverfrequencyProtectionTime | SecondOverfrequencyProtectionValue | SecondOverfrequencyProtectionTime | ThirdOverfrequencyProtectionValue | ThirdOverfrequencyProtectionTime | FirstUnderfrequencyProtectionValue | FirstUnderfrequencyProtectionTime | SecondUnderfrequencyProtectionValue | SecondUnderfrequencyProtectionTime | ThirdUnderfrequencyProtectionValue | ThirdUnderfrequencyProtectionTime | FirstOverfrequencyProtectionTimeHi（注:该寄存器与一级过频保护时间组合成32位寄存器使用） | SecondOverfrequencyProtectionTimeHi（注:该寄存器与二级过频保护时间组合成32位寄存器使用） | ThirdOverfrequencyProtectionTimeHi（注:该寄存器与三级过频保护时间组合成32位寄存器使用） | FirstUnderfrequencyProtectionTimeHi（注:该寄存器与一级欠频保护时间组合成32位寄存器使用） | SecondUnderfrequencyProtectionTimeHi（注:该寄存器与二级欠频保护时间组合成32位寄存器使用） | ThirdUnderfrequencyProtectionTimeHi（注:该寄存器与三级欠频保护时间组合成32位寄存器使用） | RoCoFMaxLimit | RoCoFMaxProtectTime
[14 empty] | Bit0 过频一级保护使能位 Bit1 过频二级保护使能位 Bit2 过频三级保护使能位 Bit3 欠频一级保护使能位 Bit4 欠频二级保护使能位 Bit5 欠频三级保护使能位 Bit6 频率变化率保护使能位 | 额定电网频率 | 一级过频保护值 | 一级过频保护时间 | 二级过频保护值 | 二级过频保护时间 | 三级过频保护值 | 三级过频保护时间 | 一级欠频保护值 | 一级欠频保护时间 | 二级欠频保护值 | 二级欠频保护时间 | 三级欠频保护值 | 三级欠频保护时间 | 一级过频保护时间高位 | 二级过频保护时间高位 | 三级过频保护时间高位 | 一级欠频保护时间高位 | 二级欠频保护时间高位 | 三级欠频保护时间高位 | 频率变化率保护值 | 频率变化率保护时间
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [8 empty] | 0.01 | 0.01 | 10 | 0.01 | 10 | 0.01 | 10 | 0.01 | 10 | 0.01 | 10 | 0.01 | 10 | 1 | 1 | 1 | 1 | 1 | 1 | 0.01 | 10
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [8 empty] | Hz | Hz | ms | Hz | ms | Hz | ms | Hz | ms | Hz | ms | Hz | ms | [6 empty] | Hz/s | ms
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | ≤100ms | 无 | 无 | 无 | 无 | 47.5Hz | ≤100ms | 无 | 无 | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 60 | 52 | 60 | 70 | 10 | 47.5 | 60 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 旧4110标准 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.5HZ | 100ms | 52.5Hz | 60ms | 无 | 无 | 47.5HZ | 100ms | 45HZ | 60ms不使能 | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.5 | 100 | 52.5 | 60 | 70 | 10 | 47.5 | 100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 德国该标准已撤销 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | ≤200ms | 无 | 无 | 无 | 无 | 47.5Hz | ≤200ms | 无 | 无 | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 52 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.5HZ | 100ms | 52.5Hz | 60ms | 无 | 无 | 47.5HZ | 100ms | 45HZ | 60ms不使能 | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.5 | 100 | 52.5 | 60 | 70 | 10 | 47.5 | 100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.5HZ | 100ms | 52.5Hz | 60ms | 无 | 无 | 47.5HZ | 100ms | 45HZ | 60ms不使能 | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.5 | 100 | 52.5 | 60 | 70 | 10 | 47.5 | 100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2Hz | （100ms+100ms*3%的误差）±20ms | 51.5Hz | （100ms+100ms*3%的误差）±20ms | 无 | 无 | 49.8Hz | （100ms+100ms*3%的误差）±20ms | 47.5 | （100ms+100ms*3%的误差）±20ms | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2 | 100 | 51.5 | 100 | 70 | 10 | 49.8 | 100 | 47.5 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 1、正标 2、系统电压≤1KV | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2Hz | （150ms+150ms*3%的误差）±20ms | 51.5Hz | （1000ms+1000ms*3%的误差）±20ms | 无 | 无 | 49.8Hz | （150ms+150ms*3%的误差）±20ms | 47.5Hz | （4000ms+4000ms*3%的误差）±20ms | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2 | 150 | 51.5 | 1000 | 70 | 10 | 49.8 | 150 | 47.5 | 4000 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 无 | 无 | 51.5Hz | （1000ms+1000ms*3%的误差）±20ms | 无 | 无 | 无 | 无 | 47.5 | （4000ms+4000ms*3%的误差）±20ms | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 51.5 | 1000 | 51.5 | 1000 | 70 | 10 | 47.5 | 4000 | 47.5 | 4000 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 50.2Hz | （100ms+100ms*3%的误差）±20ms | 51.5Hz | （100ms+100ms*3%的误差）±20ms | 无 | 无 | 49.8Hz | （100ms+100ms*3%的误差）±20ms | 47.5 | （100ms+100ms*3%的误差）±20ms | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 50.2 | 100 | 51.5 | 100 | 70 | 10 | 49.8 | 100 | 47.5 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[34 empty] | 2.5 | 60
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压 | [28 empty] | 2.5 | 60
[7 empty] | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2Hz | （150ms+150ms*3%的误差）±20ms | 51.5Hz | （1000ms+1000ms*3%的误差）±20ms | 无 | 无 | 49.8Hz | （150ms+150ms*3%的误差）±20ms | 47.5Hz | （4000ms+4000ms*3%的误差）±20ms | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2 | 150 | 51.5 | 1000 | 70 | 10 | 49.8 | 150 | 47.5 | 4000 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2Hz | （150ms+150ms*3%的误差）±20ms | 51.5Hz | （1000ms+1000ms*3%的误差）±20ms | 无 | 无 | 49.8Hz | （150ms+150ms*3%的误差）±20ms | 47.5Hz | （4000ms+4000ms*3%的误差）±20ms | 无 | 无 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2 | 150 | 51.5 | 1000 | 70 | 10 | 49.8 | 150 | 47.5 | 4000 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | ≤200 | / | / | / | / | 47 | 1000-2000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 100 | 55 | 60 | 70 | 10 | 47 | 1200 | 45 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | ≤200 | / | / | / | / | 47 | 1000-2000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 140 | 52 | 140 | 70 | 10 | 47 | 1000 | 47 | 1000 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 55 | ≤200 | / | / | / | / | 45 | 5000-6000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 55 | 140 | 55 | 140 | 70 | 10 | 45 | 5000 | 45 | 5000 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤ 500 | / | / | / | / | 48 | ≥3000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 400 | 52 | 60 | 70 | 10 | 48 | 3100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤ 500 | / | / | / | / | 48 | ≥3000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 400 | 52 | 60 | 70 | 10 | 48 | 3100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤ 500 | / | / | / | / | 48 | ≥3000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 400 | 52 | 60 | 70 | 10 | 48 | 3100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Spain island | 西班牙island |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤ 500 | / | / | / | / | 47.5 | ≥3000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 400 | 52 | 60 | 70 | 10 | 47.5 | 3100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 非标低压安规文件 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤ 500 |  |  |  |  | 48 | ≥3000 | [10 empty] | 2.5 | 60
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 400 | 52 | 60 | 70 | 10 | 48 | 3100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 300-500 | 50-52 | 100-5000 | 0 | 0 | 47.5 | 300-500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 400 | 52.5 | 60 | 70 | 10 | 47.5 | 400 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 100-200 | 0 | 0 | 0 | 0 | 47.5 | 100-200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 140 | 52.5 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 默认值200ms | / | / | / | / | 47 | 默认值200ms | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 200 | 52 | 200 | 70 | 10 | 47 | 200 | 47 | 200 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50-52（默认51.5） | 100-5000（默认200） | 0 | 0 | 0 | 0 | 47-50（默认47.5） | 100-5000（默认200） | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 70 | 10 | 70 | 10 | 47.5 | 200 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50-52（默认51.5） | 100-5000（默认200） | 0 | 0 | 0 | 0 | 47-50（默认47.5） | 100-5000（默认200） | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 70 | 10 | 70 | 10 | 47.5 | 200 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | VDE0126(Greece Continent) |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47-50 | 100-100000 | 47-50 | 100-5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50.5 | 400 | 52.5 | 60 | 70 | 10 | 47.5 | 400 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | VDE0126(Greece island) |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤500 | / | / | 0 | 0 | 47.5 | ≤500 | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 400 | 52 | 60 | 70 | 10 | 47.5 | 400 | 45.5 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | ≤2000 | 0 | 0 | 0 | 0 | 48 | ≤2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 1600 | 52 | 60 | 70 | 10 | 48 | 1600 | 47 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | C10/11 | 比利时 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤200 | 0 | 0 | 0 | 0 | 47.5 | ≤200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 52 | 20 | 70 | 10 | 47.5 | 140 | 45 | 20 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | 非标低压安规文件 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤200 | 0 | 0 | 0 | 0 | 47.5 | ≤200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 70 | 10 | 70 | 10 | 47.5 | 140 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | UK-G99标准 |  |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | / | / | 52 | 500 | / | / | 47.5 | 20000 | 47 | 500 | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | 70 | 10 | 52 | 500 | 70 | 10 | 47.5 | 20000 | 47 | 500 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | UK-G98标准 |  |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | / | / | 52 | 500 | / | / | 47.5 | 20000 | 47 | 500 | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | 70 | 10 | 52 | 500 | 70 | 10 | 47.5 | 20000 | 47 | 500 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | f＞50.2Hz | ﹤0.2s | 50.5 | <200ms | / | / | f＜47.5Hz | ﹤0.2s | / | ﹤0.2s | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 00 | China | 中国 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50.5 | 100 | 50.5 | 100 | 70 | 10 | 47 | 100 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | CNS+15382-2018 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | ﹥61Hz | ＜200 | / | / | / | / | f＜59 | ＜200 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 61 | 140 | 61 | 140 | 70 | 10 | 59 | 140 | 59 | 140 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | NB/T 32004-2018 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 600000 | 45 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.01 | 900 | 70 | 10 | 70 | 10 | 48.49 | 1900 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | 50.5 | 100 | 50.5 | 100 | 70 | 10 | 49.49 | 600000 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 无 | 无 | 50.5 | <200ms | / | / | 48≤f＜49.5 | 正常运行，停机不并网 | ﹤48Hz | ﹤0.2s | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 50.5 | 100 | 50.5 | 100 | 70 | 10 | 49.49 | 600000 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[13 empty] | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 50.5 | 100 | 50.5 | 100 | 70 | 10 | 49.49 | 600000 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 中国 | 07 | China-MV | 中国-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 中国 | 08 | China-HV | 中国-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | ＞30s | 无 | 无 | / | / | 46.5 | ＞5s | 无 | 无 | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 09 | China | 中国 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 31000 | 50.5 | 100 | 70 | 10 | 46.5 | 5100 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 中国CQC B类 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 无 | 无 | 50.5 | <200ms | / | / | 48≤f＜49.5 | 正常运行，停机不并网 | ﹤48Hz | ﹤0.2s | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 50.5 | 100 | 50.5 | 100 | 70 | 10 | 49.49 | 600000 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[13 empty] | 0 | 0 | [19 empty] | 2.5 | 60
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 600000 | 45 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 中国CQC B类 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 无 | 无 | 50.5 | <200ms | / | / | 48≤f＜49.5 | 正常运行，停机不并网 | ﹤48Hz | ﹤0.2s | / | / | 0 | 0 | 0 | 0 | 0 | 0
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 50.5 | 100 | 50.5 | 100 | 70 | 10 | 49.49 | 600000 | 48 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤0.2s | / | / | / | / | 47.5 | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 00 | France | 法国 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 52 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | FRArrete23 | 法国Arrete23 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 40Hz-70Hz | 0.01s-100s | 40Hz-70Hz | 0.01s-100s | 0 | 0 | 40Hz-70Hz | 0.01s-100s | 40Hz-70Hz | 0.01s-100s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 53 | 2500 | 55 | 60 | 70 | 10 | 46 | 1000 | 45 | 600 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤0.2s | / | / | / | / | 47.5 | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 52 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | France | 法国VDE0126 | Enedis客户 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤0.2s | / | / | / | / | 47.5 | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 52 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[34 empty] | 2.5 | 60
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis | [28 empty] | 2.5 | 60
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤0.2s | / | / | / | / | 47.5 | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 140 | 52 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47-50 | 100-100000 | 47-50 | 100-5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 400 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47-50 | 100-100000 | 47-50 | 100-5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 400 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 300-500 | 0 | 0 | 0 | 0 | 47.5 | 300-500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 400 | 70 | 10 | 70 | 10 | 47.5 | 400 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 300-500 | 0 | 0 | 0 | 0 | 47.5 | 300-500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 400 | 70 | 10 | 70 | 10 | 47.5 | 400 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | <=100ms |  |  |  |  | 47.5Hz | <=100ms |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 80 | 51.5 | 140 | 70 | 10 | 47.5 | 80 | 47.5 | 140 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 14 | 日本 | 00 | [5 empty] | 0 |  |  | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Switzerland Type A | 瑞士 Type A |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 60 | 51.5 | 60 | 0 | 0 | 47.5 | 60 | 47.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 60 | 51.5 | 60 | 70 | 10 | 47.5 | 60 | 47.5 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Switzerland Type B | 瑞士 Type B |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 60 | 51.5 | 60 | 0 | 0 | 47.5 | 60 | 47.5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 60 | 51.5 | 60 | 70 | 10 | 47.5 | 60 | 47.5 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 16-17 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50438 |  | 被 EN50549替代 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 300-500 | 0 | 0 | 0 | 0 | 47.5 | 300-500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 300 | 52.5 | 60 | 70 | 10 | 47.5 | 400 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47-50 | 100-100000 | 47-50 | 100-5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 400 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47-50 | 100-100000 | 47-50 | 100-5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 400 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | IEC EN61727 | 欧洲-IEC EN61727 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51Hz | ≤0.2s | / | / | / | / | 49Hz | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 140 | 52 | 60 | 70 | 10 | 49 | 140 | 47.5 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | / | ＞61.5 | 0-160 | / | / | / | / | 57≤f<57.5 | 299000-300000 | f<57 | 0-160 | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 60 | 61.6 | 40 | 61 | 60 | 70 | 10 | 57.4 | 299020 | 56.9 | 40 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 26 | 60 | 60.5 | 80 | 61.5 | 80 | 70 | 10 | 57.5 | 299500 | 57 | 80 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 500 | / | / | / | / | 47 | 500 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 500 | 52 | 60 | 70 | 10 | 47 | 500 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 54.5 | 140 | 55 | 60 | 70 | 10 | 45.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 23 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 52 | 60 | 0 | 0 | 47 | 200 | 45 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 52 | 60 | 70 | 10 | 47 | 200 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 200ms | / | / | / | / | 47Hz | 200ms | / | / | / | / | /
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 52 | 60 | 70 | 10 | 47 | 200 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 200ms | / | / | / | / | 47Hz | 200ms | / | / | / | / | /
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 52 | 60 | 70 | 10 | 47 | 200 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 200ms | / | / | / | / | 47Hz | 200ms | / | / | / | / | /
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 200 | 52 | 60 | 70 | 10 | 47 | 200 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | IEC61727 | 印度-IEC61727 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51Hz | ≤0.2s | / | / | / | / | 49Hz | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 25 | 印度 | 00 | India | 印度 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 140 | 52 | 60 | 70 | 10 | 49 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 印度 | 01 | India-MV | 印度-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 印度 | 02 | India-HV | 印度-高压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 50 | ＞50.5HZ | ＜0.2s | / | / | / | / | 47.5Hz≤f＜49.5Hz（建议值49.48） | ＜10min（建议值：590000） | ＜47.5 | ＜0.2s | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 50 | 50.52 | 140 | 52 | 60 | 70 | 10 | 49.48 | 590000 | 47.4 | 140 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51Hz | ≤0.2s | / | / | / | / | 49Hz | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51 | 140 | 52 | 60 | 70 | 10 | 49 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[6 empty] | Kerala地区安规参数 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50.5HZ | ≤0.2s | / | / | / | / | 47.5Hz | ≤0.2s | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 50.5 | 140 | 52 | 60 | 70 | 10 | 47.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 61.8-62.4（不包含61.8） | ≥5min | ＜62.4 | ＜100ms | / | / | 57.6-58.2（不包含58.2） | ≥5min | ＜57.6 | ≥5s | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 61.9 | 310000 | 62.3 | 60 | 70 | 10 | 57.6 | 310000 | 56 | 5100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 61Hz | ≤200ms | / | / | / | / | 59Hz | ≤200ms | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 61 | 140 | 61 | 140 | 70 | 10 | 59 | 140 | 59 | 140 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[13 empty] | 0 | 0 | [19 empty] | 2.5 | 60
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 55 | ≤200 | / | / | / | / | 45 | 1000-2000 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 55 | 140 | 55 | 60 | 70 | 10 | 45 | 1200 | 44 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | PORTARIA Nº 140 | 巴西新安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6-63.1（默认值62.6Hz） | 10-15s（默认值10s） | 63.1≤f（默认值63.1Hz） | 0.1 | / | / | 56.9-57.4（默认值57.2Hz） | 5-25s（默认值5s） | 0<f≤56.9（默认值56.9Hz） | 0.1-1s（默认值100ms） | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6 | 10000 | 63.1 | 100 | 70 | 10 | 57.4 | 5000 | 56.9 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6-63.1（默认值62.6Hz） | 10-15s（默认值10s） | 63.1≤f（默认值63.1Hz） | 100ms | / | / | 56.9-57.4（默认值57.2Hz） | 5-25s（默认值5s） | 0<f≤56.9（默认值56.9Hz） | 0.1-1s（默认值100ms） | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6 | 10000 | 63.1 | 100 | 70 | 10 | 57.4 | 5000 | 56.9 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6-63.1（默认值62.6Hz） | 10-15s（默认值10s） | 63.1≤f（默认值63.1Hz） | 0.1 | / | / | 56.9-57.4（默认值57.2Hz） | 5-25s（默认值5s） | 0<f≤56.9（默认值56.9Hz） | 0.1-1s（默认值100ms） | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6 | 10000 | 63.1 | 100 | 70 | 10 | 57.4 | 5000 | 56.9 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6-63.1（默认值62.6Hz） | 10-15s（默认值10s） | 63.1≤f（默认值63.1Hz） | 0.1 | / | / | 56.9-57.4（默认值57.2Hz） | 5-25s（默认值5s） | 0<f≤56.9（默认值56.9Hz） | 0.1-1s（默认值100ms） | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62.6 | 10000 | 63.1 | 100 | 70 | 10 | 57.4 | 5000 | 56.9 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 斯洛伐克VSD测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 51.5HZ | 80ms | 52.5Hz | 60ms |  |  | 47.5Hz | 80ms | 45Hz | 60ms |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 51.5 | 80 | 52.5 | 60 | 70 | 10 | 47.5 | 80 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 斯洛伐克SSE测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2HZ | 80ms | 52.5HZ | 60ms |  |  | 49.8HZ | 80ms | 45HZ | 60ms |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2 | 80 | 52.5 | 60 | 70 | 10 | 49.8 | 80 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.5HZ | 180ms | 52.5HZ | 100ms |  |  | 49.5HZ | 180ms | 45HZ | 60ms |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.5 | 180 | 52.5 | 100 | 70 | 10 | 49.5 | 180 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | ≤500ms | 0 | 0 | 0 | 0 | 47.5 | ≤500ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47.5 | 400 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  | 捷克 |  | EU-EN50549-1 | 捷克（中压） |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47.5-50（建议值47.5） | ≤100 | 45 | ≤100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47.5 | 60 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Czechia | 捷克<=16A系统 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 500ms | 0 | 0 | 0 | 0 | 47.5 | 500ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 450 | 52 | 500 | 70 | 10 | 47.5 | 450 | 47.5 | 500 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Czechia | 捷克>16A系统 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | ≤100ms | 0 | 0 | 0 | 0 | 47.5 | ≤100ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 | ≥0.8kW且＜100kW | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 80 | 51.5 | 100 | 70 | 10 | 47.5 | 80 | 47.5 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 100ms | 0 | 0 | 0 | 0 | 47.5 | 100ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 100 | 70 | 10 | 70 | 10 | 47.5 | 100 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52HZ | 200ms | / | / | / | / | 47HZ | 200ms | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 200 | 70 | 10 | 70 | 10 | 47 | 200 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 32 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 54.5 | 140 | 55 | 60 | 70 | 10 | 45.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 34 |  | 00 | Norway | 挪威 | 非标低压安规文件 |  |  | 0 |  |  | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 挪威低压测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 51.6Hz | 0.1s | 52Hz | 60ms | / | / | 47.5Hz | 0.1s | 45Hz | 60ms | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 51.6 | 100 | 52 | 60 | 70 | 10 | 47.5 | 100 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 墨西哥低压测试设定值 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62Hz | 200ms | 65Hz | 60ms | / | / | 57.5Hz | 2000ms | 54Hz | 60ms | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 62 | 200 | 65 | 60 | 70 | 10 | 57.5 | 2000 | 54 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 36-37 | [18 empty] | 70 | 10 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 | ＞25A/16A | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 60 | 64.5 | 140 | 65 | 60 | 70 | 10 | 55.5 | 140 | 55 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | ≤20S | 52.5 | ≤0.5S | / | / | 47.5 | ≤20S | 47 | ≤0.5S | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 | ＜25A/16A | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 18000 | 52.5 | 450 | 70 | 10 | 47.5 | 18000 | 47 | 450 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EN50549-1 | 爱尔兰 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | ≤0.5S | / | / | / | / | 47 | ≤0.5S | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 460 | 52.5 | 450 | 70 | 10 | 47 | 420 | 45 | 450 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 1000 | / | / | / | / | 48 | 500 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 1000 | 52 | 500 | 70 | 10 | 48 | 500 | 47 | 500 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[7 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 1000 | / | / | / | / | 48 | 500 | / | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 1000 | 52 | 500 | 70 | 10 | 48 | 500 | 47 | 500 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 泰国PE安规标准 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | / | 52 | ≤100ms | / | / | 47 | / | 47 | ≤100ms | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 60 | 52 | 60 | 70 | 10 | 47 | 60 | 47 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 泰国MEA安规标准 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | / | 52 | ≤100ms | / | / | 47 | / | 47 | ≤100ms | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52 | 60 | 52 | 60 | 70 | 10 | 47 | 60 | 47 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 41 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  |  |  | 0 |  |  | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 43 |  |  |  |  | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | NRS 097-2-1 | 南非标准 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | / | / | 52 | 4.0-4.5s | / | / | / | / | 47 | ≤0.2s | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 44 | 南非 | 00 | SA | 南非 |  | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 18 | 50 | 70 | 10 | 52 | 4200 | 70 | 10 | 40 | 10 | 47 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 |  | 南非 | 01 | SA-HV | 南非-高压 | Category C: 20 MVA or higher | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | SA RPPS of C | 南非+RPPS of Category C |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 4s-4.5s | / | / | / | / | 47Hz | 200-250ms | / | / | / | / | [6 empty] | 2.5 | 60
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 4200 | 52 | 4200 | 70 | 10 | 47 | 220 | 47 | 220 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 45 |  |  |  |  | 1kV以下 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 迪拜安规标准 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52.5Hz | 0.1s±20ms |  |  |  |  | 47.5Hz | 4s±20ms |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 | 1kV-33kV | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52.5 | 80 | 55 | 60 | 70 | 10 | 47.5 | 3980 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 迪拜-电站安规标准 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52.5Hz | 0.1s |  |  |  |  | 47.5Hz | 4s |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 52.5 | 100 | 55 | 60 | 70 | 10 | 47.5 | 4000 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 47-106 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 50 | >51.5Hz | 0.10s |  |  |  |  | <48.0Hz | 1.00s | <47.5Hz | 0.10s |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 25 | 50 | 51.5 | 100 | 51.1 | 100 | 70 | 10 | 48 | 1000 | 47.5 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | ﹥10KW系统51 Hz / 1800s； ≦10KW系统50.2Hz/时间越小越好 |  | ﹥10KW系统51,5 Hz / 0,5s |  |  |  | 49Hz | 1800s | 47.49Hz | 0.5 s |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 | 特殊用户参数，暂无标准 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50.2 | 100 | 50.2 | 100 | 70 | 10 | 49 | 30530 | 47.49 | 500 | 40 | 10 | 0 | 0 | 0 | 27 | 0 | 0 | 2.5 | 60
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 11 | 50 | 51.6 | 100 | 52 | 100 | 70 | 10 | 47.4 | 100 | 47.4 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 110 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
[5 empty] | 哥伦比亚安规标准 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 61Hz | ≤200ms |  |  |  |  | 59Hz | ≤200ms |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 61 | 140 | 62 | 60 | 70 | 10 | 59 | 140 | 55 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 | 给智利电力监督局通过的安规 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 61 | 140 | 62 | 60 | 70 | 10 | 59 | 140 | 55 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  | 智利 |  | Chile | 智利 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5Hz | 100ms(默认80ms） |  |  |  |  | 47.5Hz | 100ms(默认80ms） | [10 empty] | 2.5 | 60
902 | 112 | 智利 | 00 | Chile | 智利 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 50 | 51.5 | 80 | 70 | 10 | 70 | 10 | 47.5 | 80 | 40 | 10 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 60 | 62 | 1000 | 61.6 | 60 | 70 | 10 | 58 | 1000 | 57.4 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | 客户需求参考EU-EN50549 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 500 | 52.5 | 100 | 70 | 10 | 47.3 | 500 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | 客户需求参考EU-EN50549 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 | 当地经销商要求 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 51 | 500 | 52 | 100 | 70 | 10 | 47.5 | 500 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | 客户需求参考EU General |  |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 55.5 | 140 | 56 | 60 | 0 | 0 | 45.5 | 140 | 45 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 55.5 | 140 | 56 | 60 | 70 | 10 | 45.5 | 140 | 45 | 60 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
|  |  |  | AnnexC_EN 50549-2 |  |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 50-52 | 100-100000 | 50-52 | 100-5000 | 0 | 0 | 47-50 | 100-100000 | 47-50 | 100-5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 27 | 50 | 52 | 100 | 52 | 100 | 70 | 10 | 47 | 400 | 47 | 100 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 60

## DCI保护参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | Bit0：DCI 一级保护使能位 | Bit1：DCI 二级保护使能位 | Bit3：DCI 三级保护使能位 | Bit4：DCI 测试位 | DCI Config 总使能位（自动生成） | DCIFirstProtectionValue | DCIFirstProtectionTime | DCISecondProtectionValue | DCISecondProtectionTime | DCIThirdProtectionValue | DCIThirdProtectionTime | DCITestValue1 | DCITestValue2 | DCITestValue3 | DCIFirstProtectionProportion | DCISecondProtectionProportion | DCIThirdProtectionProportion
[11 empty] | Bit0：DCI 一级保护使能位 Bit1：DCI 二级保护使能位 Bit2：DCI 三级保护使能位 Bit3：DCI 测试使能位 | DCI一级保护值 | DCI一级保护时间 | DCI二级保护值 | DCI二级保护时间 | DCI三级保护值 | DCI三级保护时间 | DCI R相测试值 | DCI S相测试值 | DCI T相测试值 | DCI一级保护比例 | DCI二级保护比例 | DCI三级保护比例
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [5 empty] | 1 | 10 | 1 | 10 | 1 | 10 | 1 | 1 | 1 | 0.01 | 0.01 | 0.01
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [5 empty] | mA | ms | mA | ms | mA | ms | mA | mA | mA | % | % | %
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | 旧4110标准 | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | 德国该标准已撤销 |  |  |  |  | 0 | [9 empty] | ＞0.5%In保护
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 1 | 1 |  |  | 3 | ＞0.5%In | ≤1s | ＞1A | ≤200ms | [5 empty] | ＞0.5%In保护
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | 1、正标 2、系统电压≤1KV | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 1 | 1 |  |  | 3 | ＞0.5%In | ≤1s | ＞1A | ≤200ms | [5 empty] | ＞0.5%In保护
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 1 | 1 |  |  | 3 | ＞0.5%In | ≤1s | ＞1A | ≤200ms | [5 empty] | ＞0.5%In保护
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压
[7 empty] | 1 | 1 |  |  | 3
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[7 empty] | 1 | 1 |  |  | 3
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
|  |  |  | ASNZS4777.2-2020 | / |  | 1 | 1 | 0 | 0 | 3 | ＞0.5%In | ≤1s | ＞1A | ≤200ms | 0 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
|  |  |  | ASNZS4777.2-2020 | / |  | 1 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
|  |  |  | ASNZS4777.2-2020 | / |  | 1 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 1 | 1 | 0 | 0 | 3 | / | / | ＞±1000 | ≤200 | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 1 | 1 | 0 | 0 | 3 | / | / | ＞±1000 | ≤200 | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 1 | 1 | 0 | 0 | 3 | / | / | ＞±1000 | ≤200 | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | Spain island | 西班牙island |  | 1 | 1 | 0 | 0 | 3 | / | / | ＞±1000 | ≤200 | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[6 empty] | 非标低压安规文件 | 1 | 1 | 0 | 0 | 3 | / | / | ＞±1000 | ≤200 | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 1000 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | ＞0.5%In | / | / | / | / | / | / | / | / | /
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | VDE0126(Greece Continent) |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | VDE0126(Greece island) |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压
|  |  |  | C10/11 | 比利时 |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压
[6 empty] | 非标低压安规文件 | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | UK-G99标准 |  |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | UK-G98标准 |  |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 00 | China | 中国 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | CNS+15382-2018 | / |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
NB/T 32004-2018
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 中国 | 07 | China-MV | 中国-中压
902 |  | 中国 | 08 | China-HV | 中国-高压
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 09 | China | 中国 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
中国CQC B类
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 中国CQC B类 |  | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 00 | France | 法国 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | FRArrete23 | 法国Arrete23 |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | France | 法国VDE0126 | Enedis客户 | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 1 | 1 | 0 | 0 | 3
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 14 | 日本 | 00 |  |  |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[12 empty] | 210（0.6%） |  | 700（3%） | 160
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 1 | 1 | 0 | 0 | 3 | 210 | 800 | 700 | 160 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[12 empty] | 210（0.6%） |  | 700（3%） | 160
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 1 | 1 | 0 | 0 | 3 | 210 | 800 | 700 | 160 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 16-17 | [10 empty] | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50438 |  | 被 EN50549替代 | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | IEC EN61727 | 欧洲-IEC EN61727 |  | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | /
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 1 | 1 | 0 | 0 | 3 | 1000 | 180 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | / | / |  | 1 | 1 | 0 | 0 |  | ＞0.5%In | ≤1s | ±1A | ≤200ms | / | / | / | / | / | ＞0.5%In保护 | / | /
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 0 | 1 | 0 | 0 | 2 | 720 | 800 | 1000 | 500 | 1200 | 100 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | / | / |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压
|  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压
902 | 23 | [5 empty] | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
[7 empty] | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 1 |  |  | 3 | [9 empty] | ＞0.5%In保护
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
|  |  |  | IEC61727 | 印度-IEC61727 |  | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | /
902 | 25 | 印度 | 00 | India | 印度 |  | 1 | 1 | 0 | 0 | 3 | 1000 | 180 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 印度 | 01 | India-MV | 印度-中压
902 |  | 印度 | 02 | India-HV | 印度-高压
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 1 | 1 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 0.5 | / | /
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | /
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 1 | 1 | 0 | 0 | 3 | 1000 | 180 | 1000 | 180 | 1000 | 180 | 0 | 0 | 0 | 0.7 | 3 | 5
[6 empty] | Kerala地区安规参数 | 1 | 1 | 0 | 0 | 3 | ±1A | ≤0.2s | / | / | / | /
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 1 | 1 | 0 | 0 | 3 | 1000 | 180 | 1000 | 180 | 1000 | 180 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | 1 |  |  |  | 1 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压
[7 empty] | 1 | 1 | 0 | 0 | 3
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | ASNZS4777.2-2020 | / |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.6 | 3 | 5
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 1 | 1 | 0 | 0 | 3 | ＞0.5%In保护 | ≤1s | [7 empty] | ＞0.5%In保护
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 1 | 1 | 0 | 0 | 3
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | PORTARIA Nº 140 | 巴西230安规标准 |  | 1 | 1 | 0 | 0 | 3 | ＞0.5%In保护 | ≤1s | [7 empty] | ＞0.5%In保护
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
|  |  |  | PORTARIA Nº 140 | 巴西254安规标准 |  | 1 | 1 | 0 | 0 | 3 | ＞0.5%In保护 | ≤1s | [7 empty] | ＞0.5%In保护
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288
[5 empty] | 斯洛伐克VSD测试设定值 |  | 1 | 1 | 0 | 0 | 3
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 斯洛伐克SSE测试设定值 |  | 1 | 1 | 0 | 0 | 3
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 1 | 1 | 0 | 0 | 3
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  | 捷克 |  |  | 捷克（中压） |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | Czechia | 捷克<=16A系统 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | Czechia | 捷克>16A系统 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[7 empty] | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 32 | [9 empty] | 0 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 挪威 | 00 | Norway | 挪威 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 1 | 1 | 0 | 0 | 3
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 墨西哥低压测试设定值 |  | 1 | 1 | 0 | 0 | 3
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 36-37 | [5 empty] | 1 |  |  |  | 1 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[6 empty] | ＞25A/16A | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | /
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 泰国PEA安规标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 1 | 1 | 0 | 0 | 3
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 泰国MEA安规标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 1 | 1 | 0 | 0 | 3
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 41 | [9 empty] | 0 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 43 | [9 empty] | 0 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 1 | 1 | 0 | 0 | 3 | ＞ 0.5%In | ≤500 | / | / | / | / | / | / | / | / | / | /
902 | 44 | 南非 | 00 | SA | 南非 |  | 1 | 1 | 0 | 0 | 3 | 150 | 500 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 |  | 南非 | 01 | SA-HV | 南非-高压
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | 1 | 1 | 0 | 0 | 3 | ＞ 0.5%In | ≤500 | / | / | / | / | / | / | / | / | / | /
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 1 | 1 | 0 | 0 | 3 | 150 | 500 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 45 | [9 empty] | 0 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 迪拜安规标准 | 1kV以下 | 1 | 1 | 0 | 0 | 3 | ＞0.5%In | ≤1s | ＞1A | ≤200ms | [5 empty] | ＞0.5%In
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 1 | 1 | 0 | 0 | 3 | ＞0.5%In | ≤1s | ＞1A | ≤200ms | [5 empty] | ＞0.5%In
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.5 | 3 | 5
902 | 47-106 | [9 empty] | 0 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 0 | 1 | 0 | 0 | 2
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 0 | 1 | 0 | 0 | 2 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 0 | 1 | 0 | 0 | 2
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 0 | 1 | 0 | 0 | 2 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 110 | [9 empty] | 0 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
[5 empty] | 哥伦比亚安规标准 |  | 1 | 1 | 0 | 0 | 3
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | [5 empty] | / | / | / | / | / | / | / | / | / | / | / | /
902 | 112 | 智利 | 00 | Chile | 智利 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
客户需求参考EU-EN50549
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
客户需求参考EU-EN50549
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5
|  |  |  | AnnexC_EN 50549-2 |  |  | 1 | 1 | 0 | 0 | 3 | / | / | / | / | / | / | / | / | / | / | / | /
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 1 | 1 | 0 | 0 | 3 | 150 | 800 | 500 | 100 | 800 | 10 | 0 | 0 | 0 | 0.7 | 3 | 5

## 远程及有功参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | Bit0：有功降载使能位 | Bit1：远程开关机使能位 | Bit2：过压降载使能位 | Bit3：过压充电降载 | Bit4：欠压降充电功率使能位 | Bit5：DRM0使能位 | Bit6：逻辑接口（DRM1-8）使能位 | Bit7：防逆流过载使能位 | Bit8：电压降载PT曲线使能位 | Bit9：远程开关机降载速率控制使能位 | Bit10：CLS防逆流使能位 | Remote Config 总使能位（自动生成） | ActiveOutputLimit | ActiveOutputDownSpeed | GridVoltageDropStart | GridVoltageDropStop | GridVoltageDropMinPower | OvervoltageDownSpeed | ChgDerateVoltStart | ChgDerateVoltEnd | ChgDerateMinPower | PowerForLogic1 | PowerForLogic2 | PowerForLogic3 | PowerForLogic4 | PowerForLogic5 | PowerForLogic6 | PowerForLogic7 | PowerForLogic8 | RefluxPower | RefluxOVloadTime | LogicDerateSpeed | LogicReloadSpeed | VoltageDerateResponseTime | PowerDownSpeed | CLSRemote Config | CLSExportCurrentLimit | CLSImportCurrentLimit | CLSCurrentLimitTime | CLSCurrentProtectTime
[18 empty] | Bit0：有功降载使能位 Bit1：远程开关机使能位 Bit2：过压降载使能位 Bit3：过压充电降载 Bit4：欠压降充电功率使能位 Bit5：DRM0使能位 Bit6：逻辑接口（DRM1-8）使能位 Bit7：防逆流过载使能位 Bit8：电压降载PT曲线使能位 | 有功输出百分比 | 有功降载速率 | 电网过压降载起始点 | 电网过压降载终止点 | 电网过压降载截止功率 | 过压降载速率 | 电网欠压降载起始点 | 电网欠压降载终止点 | 电网欠压降载截止功率 | 逻辑接口1对应功率 | 逻辑接口2对应功率 | 逻辑接口3对应功率 | 逻辑接口4对应功率 | 逻辑接口5对应功率 | 逻辑接口6对应功率 | 逻辑接口7对应功率 | 逻辑接口8对应功率 | 防逆流功率（VDE4105安规并网功率上限） | 防逆流过载时间（VDE4105安规逆流过载脱网时间） | 逻辑接口降载速率 | 逻辑接口回载速率 | 电压降载时间 | 远程开关机降载速率 | Bit0：CLS家用设备选择位（0：家用设备，1：非家用设备） Bit1：CLS低功耗状态锁定使能位（低功耗：电流限制为额定电流的0.1%） | CLS防逆流输出电流限制百分比 | CLS防逆流输入电流限制百分比 | CLS防逆流PCC电流限制时间 | CLS防逆流PCC电流保护时间
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [12 empty] | 0.1 | 1 | 0.1 | 0.1 | 1 | 1 | 0.1 | 0.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 1 | 1 | 1 | 1 |  | 1 | 1 | 10 | 10
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [12 empty] | % | %Pn/min | V | V | % | %Pn/min | V | V | % | % | % | % | % | % | % | % | % | % | ms | %Pn/min | %Pn/min | 秒 | %Pn/min |  | % | % | ms | ms
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 0 | 1 |  |  |  | 0 | 1 | 0 |  | 0 | 0 | 66 |  | 0.33-0.66/s | [7 empty] | 0 |  |  |  | 0
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 旧4110标准 | 0 | 1 |  |  |  | 0 | 1 | 0 |  | 0 | 0 | 66 | [9 empty] | 0 |  |  |  | 0 | [8 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 德国该标准已撤销 | 0 | 1 |  |  |  | 0 | 1 | 0 |  | 0 | 0 | 66 | [9 empty] | 0 |  |  |  | 0 | [8 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 00 | 德国 | 02 | BDEW | 德国0126 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 0 | 1 |  |  |  | 0 | 1 | 0 |  | 0 | 0 | 66 | [9 empty] | 0 |  |  |  | 0 | [8 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 0 | 1 |  |  |  | 0 | 1 | 0 |  | 0 | 0 | 66 | [9 empty] | 0 |  |  |  | 0 | [8 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 0 | 1 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 6 |  |  | 110%Un | 无 | ＜20%Pn | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 253 | 265 | 18 | 22 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 1、正标 2、系统电压≤1KV | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | 110%Un | 无 | ＜20%Pn | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 253 | 265 | 18 | 22 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | 110%Un | 无 | ＜20%Pn | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 253 | 265 | 18 | 22 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | 110%Un | 无 | ＜20%Pn | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 253 | 265 | 18 | 22 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[17 empty] | 0 | [24 empty] | 0 | 100 | 100 | 15000 | 60000
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压 | [11 empty] | 0 | [24 empty] | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | 110%Un | 无 | ＜20%Pn | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 342 | 358 | 18 | 22 | 284 | 277 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  | 110%Un | 无 | ＜20%Pn | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 317 | 332 | 18 | 22 | 263 | 257 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 |  |  | 110%Un | 113.04%Un | ＜20%Pn | 6000 | 93.48%Un | 90%Un | -20 | 0 | ＜50 | ＜75 |  | 0 | ＜50 | ＜75 | 100 | 100可调 | / | 16.67 | 16.67 | ＜10s | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 253 | 260 | 18 | 600 | 210 | 205 | -20 | 0 | 47 | 72 | 100 | 0 | 47 | 72 | 100 | 100 | 3000 | 16 | 16 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | ASNZS4777.2-2020 | / |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 108.70%Un | 113.04%Un | ＜20%Pn | 6000 | 93.48%Un | 84.78%Un | -20 | 0 | ＜50 | ＜75 |  | 0 | ＜50 | ＜75 | 100 | 100可调 | / | 16.67 | 16.67 | ＜10s | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 250 | 260 | 18 | 600 | 215 | 195 | -20 | 0 | 47 | 72 | 100 | 0 | 47 | 72 | 100 | 100 | 3000 | 16 | 16 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | ASNZS4777.2-2020 | / |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 110%Un | 113.04%Un | ＜20%Pn | 6000 | 93.48%Un | 90%Un | -20 | 0 | ＜50 | ＜75 |  | 0 | ＜50 | ＜75 | 100 | 100可调 | / | 16.67 | 16.67 | ＜10s | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 253 | 260 | 18 | 600 | 210 | 205 | -20 | 0 | 47 | 72 | 100 | 0 | 47 | 72 | 100 | 100 | 3000 | 16 | 16 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | Spain island | 西班牙island |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 非标低压安规文件 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 140 | 143.5 | 20 | 600 | 116 | 113 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115.2%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 264.5 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | VDE0126(Greece Continent) |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.70%Un | 115.22%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | RD1699 | 西班牙 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115.2%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | C10/11 | 比利时 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 1.08Un | 降载幅度:＞10%Pn/1%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 248.4 | 255.3 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | 非标低压安规文件 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 1.08Un | 降载幅度:＞10%Pn/1%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 137 | 143.5 | 18 | 600 | 116 | 113 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | UK-G99标准 |  |  | 0 | 1 | 0 | 0 | 0 | / | 1 | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | ＞1200 | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | UK-G98标准 |  |  | 0 | 1 | 0 | 0 | 0 | / | 1 | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | ＞1200 | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 00 | China | 中国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | CNS+15382-2018 | / |  | / | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | NB/T 32004-2018 |  |  | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 285 | 305 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 285 | 305 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 |  |  |  | 270 | 274 | [18 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 100 | 270 | 274 | 0 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 中国 | 07 | China-MV | 中国-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 中国 | 08 | China-HV | 中国-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 09 | China | 中国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 中国CQC B类 |  | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 中国CQC B类 |  | / | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 00 | France | 法国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | FRArrete23 | 法国Arrete23 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 110%Un | 113.04%Un | 20 | 600 | 91.30%Un | 89.13%Un | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | France | 法国VDE0126 | Enedis客户 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[17 empty] | 0 | [24 empty] | 0 | 100 | 100 | 15000 | 60000
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis | [11 empty] | 0 | [24 empty] | 0 | 100 | 100 | 15000 | 60000
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 2100 | 2050 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.70%Un | 115.22%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.70%Un | 115.22%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 110%Un | / | ＜20%Pn | 5min内降到＜20%Pn | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | 5s内降为0 | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 253 | 260 | 18 | 20 | 210 | 205 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 110%Un | / | ＜20%Pn | 5min内降到＜20%Pn | / | / | / | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | 5s内降为0 | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 253 | 260 | 18 | 20 | 210 | 205 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | 奥地利TOR安规标准 |  | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 326 | / | / | 110%Un | 112%Un | 0 | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | / | / | 15 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 326 | 100 | 100 | 253 | 257.6 | 0 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 15 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 14 | 日本 | 00 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | 0 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | 0 | [22 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 16-17 | [14 empty] | 0 | 0 | 0 | [22 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50438 |  | 被 EN50549替代 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115.2%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 250 | 265 | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | IEC EN61727 | 欧洲-IEC EN61727 |  | 0 | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | 20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EN50549-1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 23 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 110%Un | 88.46%Un | 20 | 600 | 109.52%Un | 112.20%Un | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 0 | 1 |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 2 |  | 0.33-0.66/s | [7 empty] | 0 |  |  |  | 0 | [5 empty] | 3000 |  |  | 3000
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 3000 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 0 | 1 |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 2 |  | 0.33-0.66/s | [7 empty] | 0 |  |  |  | 0 | [5 empty] | 3000 |  |  | 3000
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 3000 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 塞浦路斯等级C | P > 120kWp | 0 | 1 |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 2 |  | 0.33-0.66/s | [7 empty] | 0 |  |  |  | 0 | [5 empty] | 3000 |  |  | 3000
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 3000 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 0 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | IEC61727 | 印度-IEC61727 |  | 0 | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 25 | 印度 | 00 | India | 印度 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 印度 | 01 | India-MV | 印度-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 印度 | 02 | India-HV | 印度-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 8 | 0 | 100 | 100 | 15000 | 60000
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 514 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 8 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 0 | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | Kerala地区安规参数 | 0 | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | [9 empty] | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | ASNZS4777.2-2020 |  |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 105.22%Un | 108.70%Un | 20 | 6000 | 97.39%Un | 93.91%Un | -20 | 0 | ＜50 | ＜75 | 100 | 0 | ＜50 | ＜75 | 100 | 100可调 | / | 16.67 | 16.67 | ＜10s | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 100 | 100 | 242 | 250 | 18 | 600 | 224 | 216 | -20 | 0 | 47 | 72 | 100 | 0 | 47 | 72 | 100 | 100 | 3000 | 16 | 16 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 斯洛伐克VSD测试设定值 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 斯洛伐克SSE测试设定值 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 109%Un | 111%Un | 0 | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 255 | 0 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  | 捷克 |  | EU-EN50549-1 | 捷克（中压） |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | Czechia | 捷克<=16A系统 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | / | 109%Un | 111%Un | 0 | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250.7 | 255.3 | 0 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | Czechia | 捷克>16A系统 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | / | 109%Un | 111%Un | 0 | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250.7 | 255.3 | 0 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | / | 109%Un | 111%Un | 0 | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250.7 | 255.3 | 0 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 32 | [15 empty] | 0 | [24 empty] | 0 | 100 | 100 | 15000 | 60000
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 挪威 | 00 | Norway | 挪威 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 墨西哥低压测试设定值 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 36-37 | [14 empty] | 0 | 0 | 0 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[6 empty] | ＞25A/16A | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115.2%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115.2%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 0 | 0 | 0 | / | 1 | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | ＞1200 | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[7 empty] | 0 | 1 | 0 | 0 | 0 | / | 1 | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | ＞1200 | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 66 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 泰国PEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 泰国MEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 41 | [14 empty] | 0 | 0 | 0 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 43 | [14 empty] | 0 | 0 | 0 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 44 | 南非 | 00 | SA | 南非 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[16 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 |  | 南非 | 01 | SA-HV | 南非-高压 | [10 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 45 | [14 empty] | 0 | 0 | 0 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 迪拜安规标准 | 1kV以下 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | [17 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 265 | 18 | 22 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 265 | 18 | 22 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 47-106 | [14 empty] | 0 | 0 | 0 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.70%Un | 115.22%Un | ＜20%Pn | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.70%Un | 115.22%Un | ＜20%Pn | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 110 | [14 empty] | 0 | 0 | 0 | [19 empty] | 3000 | 3000 |  | 3000 | 0 | 100 | 100 | 15000 | 60000
[5 empty] | 哥伦比亚安规标准 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 253.1 | 18 | 9 | 210 | 205 | -27 | 0 | 30 | 60 | 100 | 0 | 0 | 0 | 0 | 60 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 253.1 | 18 | 9 | 210 | 205 | -27 | 0 | 30 | 60 | 100 | 0 | 0 | 0 | 0 | 60 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | 0 | 1 | / | / | / | / | / | / | / | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 112 | 智利 | 00 | Chile | 智利 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 253.1 | 18 | 9 | 210 | 205 | -27 | 0 | 30 | 60 | 100 | 0 | 0 | 0 | 0 | 60 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | 客户需求参考EU-EN50549 | [11 empty] | 0 | 0 | [23 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | 客户需求参考EU-EN50549 | [11 empty] | 0 | 0 |  |  |  | 108.696%Un | 115.217%Un | [18 empty] | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 100 | 253 | 260 | 20 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 30 | 60 | 100 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000
|  |  |  | AnnexC_EN 50549-2 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | / | / | 108.7%Un | 115.2%Un | ＜20%Pn | 无 | 无 | 无 | 无 | / | / | / | / | 0 | / | / | / | / | / |  | / | / | 3000 | 0 | 100 | 100 | 15000 | 60000
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 70 | 100 | 100 | 250 | 265 | 18 | 600 | 210 | 205 | -20 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 | 3000 | 3000 | 3000 | 10 | 3000 | 0 | 100 | 100 | 15000 | 60000

## 频率有功参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | Bit0：过频输出降载使能 | Bit1：欠频J加载使能 | Bit2：过频回载使能 | Bit3：欠频回载使能 | Bit4：过频从额定功率开始降载使能 | Bit5：当前功率计算降载斜率使能 | Bit6：储能分段曲线使能 | Bit7：最大功率计算使能 | Bit8：欠频从额定功率开始降载使能 | Bit9: 过欠频回载速率使能位 | Bit12-13：降载模式（0斜率模式/1频率范围模式） （不需要填写） | Bit12 | Bit13（预留） | Bit14：过频降载功率截止使能位 | FrequencyDerateConfig 总使能位（自动生成） | OverfrequencyStart | OverfrequencyEnd | OverfrequencySlope | OverfrequencyResponseDelay | OverfrequencyReloadDelay | OverfrequencyReloadStart | OverfrequencyReloadSpeed | UnderfrequencyStart | UnderfrequencyEnd | UnderfrequencySlope | UnderfrequencyResponseDelay | UnderfrequencyReloadDelay | UnderfrequencyReloadStart | UnderfrequencyReloadSpeed | FrequencyRecoverMax | FrequencyRecoverMin | （储能）OverfrequencyStart | （储能）OverfrequencyEnd | （储能）OverfrequencySlope | （储能）OverfrequencyResponseDelay | （储能）OverfrequencyReloadDelay | （储能）OverfrequencyReloadStart | （储能）OverfrequencyReloadSpeed | （储能）UnderfrequencyStart | （储能）UnderfrequencyEnd | （储能）UnderfrequencySlope | （储能）UnderfrequencyResponseDelay | （储能）UnderfrequencyReloadDelay | （储能）UnderfrequencyReloadStart | （储能）UnderfrequencyReloadSpeed | （储能）FrequencyRecoverMax | （储能）FrequencyRecoverMin | （储能）OverFRTFrequency | （储能） UnderFRTFrequency
[21 empty] | Bit0：过频输出降载使能 Bit1：欠频输入降载使能 Bit2：过频回载使能 Bit3：欠频回载使能 Bit4：从额定功率开始降载使能 Bit5：当前功率计算降载斜率使能 Bit6：储能分段曲线使能 Bit12-13：降载模式（0斜率模式/1频率范围模式） | 过频降载起始频率 | 过频降载截止频率。频率范围模式有效 | 过频降载斜率百分比。斜率模式有效 德标slope=1/(s*fn) | 过频降载启动等待时间 | 过频回载前等待时间 | 过频降载回载频率。禁止过频回载时生效。 | 过频回载速率百分比 | 欠频降载起始频率 | 欠频降载截止频率。频率范围模式有效 | 欠频降载斜率百分比。斜率模式有效 | 欠频降载启动等待时间 | 欠频回载前等待时间 | 欠频降载回载频率。禁止欠频回载时生效。 | 欠频回载速率百分比 | 退出降载最高频率。过欠频共用。允许过频回载时生效 | 退出降载最低频率。过欠频共用。允许欠频回载时生效 | （储能） 过频降载起始频率 | （储能）过频降载截止频率。频率范围模式有效 | （储能）过频降载斜率百分比。斜率模式有效 德标slope=1/(s*fn) | （储能）过频降载启动等待时间 | （储能）过频回载前等待时间 | （储能）过频降载回载频率。禁止过频回载时生效。 | （储能）过频回载速率百分比 | （储能）欠频降载起始频率 | （储能） 欠频降载截止频率。频率范围模式有效 | （储能）欠频降载斜率百分比。斜率模式有效 | （储能）欠频降载启动等待时间 | （储能）欠频回载前等待时间 | （储能）欠频降载回载频率。禁止欠频回载时生效。 | （储能）欠频回载速率百分比 | （储能）退出降载最高频率。过欠频共用 | （储能）退出降载最低频率。过欠频共用 | （储能）过频降载功率穿越频率点。使能储能分段曲线时有效。 | （储能）欠频降载功率穿越频率点。使能储能分段曲线时有效。
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [15 empty] | 0.01 | 0.01 | 1 | 10 | 10 | 0.01 | 1 | 0.01 | 0.01 | 1 | 10 | 10 | 0.01 | 1 | 0.01 | 0.01 | 0.01 | 0.01 | 1 | 10 | 10 | 0.01 | 1 | 0.01 | 0.01 | 1 | 10 | 10 | 0.01 | 1 | 0.01 | 0.01 | 0.01 | 0.01
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [15 empty] | Hz | Hz | %Pn/Hz | ms | ms | Hz | %Pn/min | Hz | Hz | %Pn/Hz | ms | ms | Hz | %Pn/min | Hz | Hz | Hz | Hz | %Pn/Hz | ms | ms | Hz | %Pn/min | Hz | Hz | %Pn/Hz | ms | ms | Hz | %Pn/min | Hz | Hz | Hz | Hz
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 |  |  |  | 0 | 37 | 50.2 |  | 40 | 0 | ＞60s | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | ＞60000 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 40 | 0 | ＞60s | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | ＞60000 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 610000 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 30000 | 49.85 | 9 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 610000 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 30000 | 49.85 | 10 | 50.2 | 49.85 | 51 | 49
[6 empty] | 旧4110标准 | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 |  |  |  | 0 | 37 | 50.2 |  | 40 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 40 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 30000 | 49.85 | 9 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 30000 | 49.85 | 10 | 50.2 | 49.85 | 51 | 49
[6 empty] | 德国该标准已撤销 | 1 |  | 1 |  |  | 1 |  |  | 0 | 0 |  |  |  | 0 | 37
902 | 00 | 德国 | 02 | VDE4105 | 德国0126 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 610000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 9 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 610000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 |  |  |  | 0 | 37 | 50.2 |  | 40 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 100 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 100 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 0 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 0 | 49.85 | 9 | 50.2 | 49.85 | 50.2 |  | 100 | 0 | 0 | 50.2 | 9 | 49.8 | 47.5 | 100 | 0 | 0 | 49.85 | 10 | 50.2 | 49.85 | 51 | 49
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 |  |  |  | 0 | 37 | 50.2 |  | 40 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 100 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 100 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 0 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 0 | 49.85 | 9 | 50.2 | 49.85 | 50.2 |  | 100 | 0 | 0 | 50.2 | 9 | 49.8 | 47.5 | 100 | 0 | 0 | 49.85 | 10 | 50.2 | 49.85 | 51 | 49
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 1 |  |  |  |  | 1 |  |  | 0 | 0 | 1 |  |  | 0 | 33 | 50.2 | 51.5 | 77 |  | ≥300s | 50.1 | 起始功率<25%Pn时,回载速率为5%Pn/min,起始功率>25%Pn时,回载速率为5%-20%Pn/min | 49.8/49.6储能机器有两个进入点 | 49.1 | 133 | 0 | ＞300s | 49.85 | 9 |  |  | 50.2 | 51.5 | 77 |  | ≥300s | 50.1 | 20%(Pmem-Pmin)/min Pmem:过频触发频率点对应的功率 Pmin:过频降载截止功率 | 49.8/49.6储能机器有两个进入点 | 49.1 | 133 | 0 | ＞300s | 49.9 | 20%(Pmem-Pmin)/min Pmem:欠频触发频率点对应的功率 Pmin:过频降载截止功率
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4129 | 50.2 | 51.5 | 77 | 0 | 310000 | 50.1 | 5 | 49.8 | 49.1 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 50.2 | 51.5 | 77 | 0 | 310000 | 50.1 | 20 | 49.8 | 49.1 | 133 | 0 | 30000 | 49.9 | 20 | 50.1 | 49.85 | 51 | 49
[6 empty] | 1、正标 2、系统电压≤1KV | 1 |  |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 0 | 33 | 50.2 |  | 77 |  | ≥300s | 50.1 | 20%(Pmem-Pmin)/min Pmem:欠频触发频率点对应的功率 Pmin:过频降载截止功率 | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9 |  |  | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 20 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 51 | 49
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 1 |  |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 0 | 33 | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9 |  |  | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 51 | 49
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 1 |  |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 0 | 33 | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9 |  |  | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 51 | 49
[16 empty] | 0 |  |  |  | 0
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压 | [10 empty] | 0 |  |  |  | 0
[7 empty] | 1 |  |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 0 | 33 | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9 |  |  | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 51 | 49
[7 empty] | 1 |  |  |  |  | 1 |  |  | 0 | 0 |  |  |  | 0 | 33 | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9 |  |  | 50.2 |  | 77 |  | ≥300s | 50.1 | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | 49.8 | 51.5 | 133 | 0 | ＞300s | 49.85 | 9
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 50.2 | 52 | 77 | 0 | 310000 | 50.1 | 9 | 49.8 | 51.5 | 133 | 0 | 30000 | 49.85 | 9 | 50.1 | 49.85 | 51 | 49
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.25 | 52 | /（标准是按当前值和频率差值计算） | 0 | ＞20000 | 50.15 | 16.67 | 49.75 | 48 | / | 0 | ＞20000 | 49.85 | 16.67 | 50.15 | 49.85 | 50.25 | 52 | / | 0 | ＞20000 | 50.15 | 16.67 | 49.75 | 48 | / | 0 | ＞20000 | 49.85 | 16.67 | 50.15 | 49.85
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.25 | 52 | 0 | 0 | 610000 | 50.15 | 17 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.15 | 49.85 | 50.25 | 52 | 40 | 0 | 610000 | 50.15 | 17 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.15 | 49.85 | 50.75 | 49
|  |  |  | ASNZS4777.2-2020 | / |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.15 | 52 | / | 0 | ＞20000 | 50.05 | 16.67 | 49.85 | 48 | / | 0 | ＞20000 | 49.95 | 16.67 | 50.15 | 49.85 | 50.15 | 52 | / | 0 | ＞20000 | 50.05 | 16.67 | 49.85 | 48 | / | 0 | ＞20000 | 49.95 | 16.67 | 50.15 | 49.85
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.15 | 52 | 40 | 0 | 30000 | 50.05 | 17 | 49.85 | 48 | 54 | 0 | 30000 | 49.95 | 16 | 50.15 | 49.85 | 50.15 | 52 | 40 | 0 | 30000 | 50.05 | 17 | 49.85 | 48 | 54 | 0 | 30000 | 49.95 | 16 | 50.15 | 49.85 | 50.75 | 49
|  |  |  | ASNZS4777.2-2020 | / |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.5 | 53 | / | 0 | ＞20000 | 50.45 | 16.67 | 49.5 | 47 | / | 0 | ＞20000 | 49.55 | 16.67 | 50.5 | 49.8 | 50.5 | 53 | / | 0 | ＞20000 | 50.45 | 16.67 | 49.5 | 47 | / | 0 | ＞20000 | 49.55 | 16.67 | 50.5 | 49.8
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.5 | 53 | 40 | 0 | 30000 | 50.45 | 17 | 49.5 | 47 | 40 | 0 | 30000 | 49.55 | 17 | 50.5 | 49.8 | 50.5 | 53 | 40 | 0 | 30000 | 50.45 | 17 | 49.5 | 47 | 40 | 0 | 30000 | 49.55 | 17 | 50.5 | 49.8 | 51.75 | 48.25
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 50.2-50.5Hz（默认50.2Hz） | 52 | 16.67%-100%(默认40%) | 0 | 0 | 50.2 | 9 | 49.5-49.8Hz（默认49.8Hz） | 48 | 16.67%-100%(默认40%) | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 0 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 50.2 | 52 | 40 | 0 | 0 | 50.2 | 9 | 49.8 | 48 | 40 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | Spain island | 西班牙island |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[6 empty] | 非标低压安规文件 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 1 | 0 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 0 |  |  |  | 0 | 49 | 50.2Hz-52Hz（默认50.2Hz） | 52 | 16.67%Pn/Hz-100%Pn/Hz（默认50%Pn/Hz） | 0 | 0 | 与降载起始频率对应50.2Hz | <10 | / | / | / | / | / | / | / | / | / | 50.2Hz-52Hz（默认50.2Hz） | 52 | 16.67%Pn/Hz-100%Pn/Hz（默认50%Pn/Hz） | 0 | 0 | 与降载起始频率对应50.2Hz | <10 | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 1 | 0 | 0 | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 50.2 | 52 | 50 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 50 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 40 | 500ms | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 40 | 500 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.5 | 52 | 50 | 500ms | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.5 | 52 | 50 | 500 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | VDE0126(Greece Continent) |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | VDE0126(Greece island) |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压 | [9 empty] | 0 | 0 |  |  |  | 0
[15 empty] | 0 | 0 |  |  |  | 0
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压 | [9 empty] | 0 | 0 |  |  |  | 0
|  |  |  | C10/11 | 比利时 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压 | [9 empty] | 0 | 0 |  |  |  | 0
[6 empty] | 非标低压安规文件 | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | UK-G99 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4 | 52 | 20 | / | / | 50.4 | / | / | / | / | / | / | / | / | / | / | 50.4 | 52 | 20 | / | / | 50.4 | / | / | / | / | / | / | / | / | / | /
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 51 | 49
|  |  |  | UK-G98 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4 | 52 | 20 | / | / | 50.4 | / | / | / | / | / | / | / | / | / | / | 50.4 | 52 | 20 | / | / | 50.4 | / | / | / | / | / | / | / | / | / | /
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 00 | China | 中国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | CNS+15382-2018 | / |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | NB/T 32004-2018 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 中国 | 07 | China-MV | 中国-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 中国 | 08 | China-HV | 中国-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 09 | China | 中国 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 中国CQC B类 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ＞50.03Hz（A类) | 50.53 |  | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[7 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 中国CQC B类 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | / | ＞50.03Hz（A类) | 50.53 | 40%（A类）0.5Hz降最大20% | ≤0.5s | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.04 | 50.53 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | / | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 00 | France | 法国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | FRArrete23 | 法国Arrete23 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | / | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | France | 法国VDE0126 | Enedis客户 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | / | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[16 empty] | 0 |  |  |  | 0
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis | [10 empty] | 0 |  |  |  | 0
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | / | 50.4 | / | 40%Pref/Hz | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 50.2Hz-50.5Hz（默认50.2Hz) | / | 16.67%-100%（默认40%） | 0 | 3000 | 50.2 | ＜10%Pn/min | / | / | / | / | / | / | / | / | / | 50.2Hz-50.5Hz（默认50.2Hz) | / | 16.67%-100%（默认40%） | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | /
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 50.2 | 52 | 40 | 0 | 3000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 50.2Hz-50.5Hz（默认50.2Hz) | / | 16.67%-100%（默认40%） | 0 | 3000 | 50.2 | ＜10%Pn/min | / | / | / | / | / | / | / | / | / | 50.2Hz-50.5Hz（默认50.2Hz) | / | 16.67%-100%（默认40%） | 0 | 0 | 50.2 | / | / | / | / | / | / | / | / | / | /
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 50.2 | 52 | 40 | 0 | 3000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 37 | 50.2Hz |  | 40% |  | 1s | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | [9 empty] | 50.2Hz |  | 40% |  | 1s | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10%
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 14 | 日本 | 00 | [7 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85
[15 empty] | 0 | 0 |  |  |  | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 16-17 | [13 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | EU-EN50438 |  | 被 EN50549替代 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | / | 40 | 0 | 0 | 50.2 | [10 empty] | 50.2 | / | 40 | 0 | 0 | 50.2
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | IEC EN61727 | 欧洲-IEC EN61727 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.2 | 62 | 40 | 0 | 1000 | 60.2 | 9 | 59.75 | 58 | 57 | 0 | 30000 | 59.85 | 17 | 60.2 | 59.85 | 60.2 | 62 | 40 | 0 | 1000 | 60.2 | 9 | 59.75 | 58 | 57 | 0 | 30000 | 59.85 | 17 | 60.2 | 59.85 | 61 | 59
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.2 | 62 | 40 | 0 | 1000 | 60.2 | 9 | 59.75 | 58 | 57 | 0 | 30000 | 59.85 | 17 | 60.2 | 59.85 | 60.2 | 62 | 40 | 0 | 1000 | 60.2 | 9 | 59.75 | 58 | 57 | 0 | 30000 | 59.85 | 17 | 60.2 | 59.85 | 61 | 59
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.5 | 52 | 40 | 0 | 0 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | / | / | / | / | / | / | / | / | / | 50.5 | 52 | 40 | 0 | 0 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | / | / | / | / | / | / | / | / | /
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.5 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.5 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
902 | 23 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[7 empty] | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 51.5 | 40% | 0 | 0 | 50.2 | 10 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 51.5 | 4 | 0 | 0 | 50.2 | 10 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 51.5 | 40 | 0 | 0 | 50.2 | 10 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 51.5 | 4 | 0 | 0 | 50.2 | 10 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 1 |  |  | 0 |  | 50.2Hz | 51.2 | 100%Pm/Hz | 0 | ＞60s | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | ＞60000 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 40 | 0 | ＞60s | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | ＞60000 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4133 | 50.2 | 51.2 | 100 | 0 | 60500 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 60500 | 49.85 | 9 | 50.2 | 49.85 | 50.2 | 51.5 | 40 | 0 | 60500 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 60500 | 49.85 | 9 | 50.2 | 49.85 | 51 | 49
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 1 |  |  | 0 |  | 50.2Hz | 51.2 | 100%Pm/Hz | 0 | ＞60s | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | ＞60000 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 40 | 0 | ＞60s | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | ＞60000 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4133 | 50.2 | 51.2 | 100 | 0 | 60500 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 60500 | 49.85 | 9 | 50.2 | 49.85 | 50.2 | 51.5 | 40 | 0 | 60500 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 60500 | 49.85 | 9 | 50.2 | 49.85 | 51 | 49
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 0 | 1 | 0 | 0 | 1 |  |  | 0 | 0 | 1 |  |  | 0 |  | 50.2Hz | 51.2 | 100%Pm/Hz | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 40 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85 | 50.2 |  | 100 | 0 | 0 | 50.2 | 降低频率就按<10%开始恢复 | 49.8 | 47.5 | 100 | 0 | 0 | ＞49.85 | ＜10% | ＜50.2 | ＜49.85
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4133 | 50.2 | 51.2 | 100 | 0 | 0 | 50.2 | 9 | 49.8 | 47.5 | 40 | 0 | 0 | 49.85 | 9 | 50.2 | 49.85 | 50.2 | 51.5 | 100 | 0 | 0 | 50.2 | 9 | 49.8 | 47.5 | 100 | 0 | 0 | 49.85 | 9 | 50.2 | 49.85 | 51 | 49
|  |  |  | IEC61727 | 印度-IEC61727 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 25 | 印度 | 00 | IEC61727 | 印度-IEC61727 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 印度 | 01 | India-MV | 印度-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 印度 | 02 | India-HV | 印度-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 1 | 1 | 1 | 1 | 0 | 1 |  |  | 1 | 0 | 0 |  |  | 0 | 303 | 50.05 | 52 | 40 | 0 | 0 | ＜50.1 | ＜10 | 49.9 | 47.5 | 40 | 0 | 0 | ＞49.9 | ＜10 | ＜50.1 | ＞49.9
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 1 | 1 | 1 | 1 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 303 | 50.05 | 52 | 40 | 0 | 0 | 50.05 | 9 | 49.9 | 47.5 | 40 | 0 | 0 | 49.95 | 9 | 50.05 | 49.95 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[6 empty] | Kerala地区安规参数 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 61 | / | 75 | / | / | / | / | / | / | / | / | / | / | / | / | / | 61 | / | 75 | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 61 | 52 | 75 | 0 | 1000 | 61 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 61 | 49.85 | 61 | 52 | 75 | 0 | 1000 | 61 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 61 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.5 | 52 | 40 | 0 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 60.5 | 52 | 40 | 0 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 51 | 49
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.2 | 52 | /（标准是按当前值和频率差值计算） | 0 | ＞20000 | 50.1 | 16.67 | 49.8 | 48 | / | 0 | ＞20000 | 49.9 | 16.67 | 50.15 | 49.85 | 50.2 | 52 | / | 0 | ＞20000 | 50.1 | 16.67 | 49.8 | 48 | / | 0 | ＞20000 | 49.9 | 16.67 | 50.15 | 49.85
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4163 | 50.2 | 52 | 1 | 0 | 30000 | 50.1 | 17 | 49.8 | 48 | 1 | 0 | 30000 | 49.9 | 17 | 50.15 | 49.85 | 50.2 | 52 | 40 | 0 | 30000 | 50.1 | 17 | 49.8 | 48 | 1 | 0 | 30000 | 49.9 | 17 | 50.15 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30%Pn/Hz(60.2Hz-62.6Hz频率段有功功率按30%Pn/Hz降载到28%Pn，62.6Hz-63.1Hz有功功率不再随着频率变化) | 500ms | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | / | 60.5HZ | / | 40% | / | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | /
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30 | 500 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 60.5 | 52 | 40 | 0 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 51 | 49
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30%Pn/Hz(60.2Hz-62.6Hz频率段有功功率按30%Pn/Hz降载到28%Pn，62.6Hz-63.1Hz有功功率不再随着频率变化) | 500ms | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | / | 60.5HZ | / | 40% | / | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | /
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30 | 500 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 60.5 | 52 | 40 | 0 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 51 | 49
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30%Pn/Hz(60.2Hz-62.6Hz频率段有功功率按30%Pn/Hz降载到28%Pn，62.6Hz-63.1Hz有功功率不再随着频率变化) | 500ms | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | / | 60.5HZ | / | 40% | / | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | /
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30 | 500 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 60.5 | 52 | 40 | 0 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 51 | 49
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30%Pn/Hz(60.2Hz-62.6Hz频率段有功功率按30%Pn/Hz降载到28%Pn，62.6Hz-63.1Hz有功功率不再随着频率变化) | 500ms | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | / | 60.5HZ | / | 40% | / | ﹥300S | 60.1HZ | <10% | / | / | / | / | / | / | / | / | /
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16421 | 60.2 | 62.6 | 30 | 500 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 60.5 | 52 | 40 | 0 | 310000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
[5 empty] | 斯洛伐克VSD测试设定值 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 斯洛伐克SSE测试设定值 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | 49.8 | / | 40 | / | 0 | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | 49.8 | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 40 | 0 | 0 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  | 捷克 |  |  | 捷克（中压） |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | 49.8 | / | 40 | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | 49.8 | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 40 | 0 | 0 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | Czechia | 捷克<=16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 40 | 0 | 0 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | Czechia | 捷克>16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 40 | 0 | 0 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 1 | 0 | 1 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | 49 | / | 2%Pn/Hz | / | / | / | / | 50.05 | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 0 | 1 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49 | 48 | 2 | 0 | 0 | 49.85 | 17 | 50.05 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[7 empty] | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 40 | 0 | 0 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.8 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 32 | [14 empty] | 0 |  |  |  | 0
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 |  | 挪威 | 00 | Norway | 挪威 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2Hz | / | 40%PN/Hz | / | / | / | / | / | / | / | / | / | / | / | / | / | 50.2Hz | / | 40%PN/Hz | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 墨西哥低压测试设定值 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60.5Hz | / | 40 | / | 300s | 60.1HZ | 0.09 | / | / | / | / | / | / | / | / | / | 60.5Hz | / | 40 | / | 300s | 60.1HZ | 0.09 | / | / | / | / | / | / | / | / | /
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60.5 | 52 | 40 | 0 | 300000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 60.5 | 52 | 40 | 0 | 300000 | 60.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 60.1 | 49.85 | 51 | 49
902 | 36-37 | [13 empty] | 0 | 0 |  |  |  | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[6 empty] | ＞25A/16A | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 |  |  |  | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 |  |  |  | 0 | 37 | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[7 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 51 | 49
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 50 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 51 | 49
[7 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 51 | 49
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2 | 52 | 50 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 50.4 | 52 | 20 | 0 | 1000 | 50.4 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.4 | 49.85 | 51 | 49
[5 empty] | 泰国PEA安规标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 泰国MEA安规标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 41 | [13 empty] | 0 | 0 |  |  |  | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 43 | [13 empty] | 0 | 0 |  |  |  | 0 | 0 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.5 | 52 | 50 | 0 | 4000 |  |  | / | / | / | / | / | / | / | / | / | 50.5 | 52 | 50 | 0 | 4000 |  |  | / | / | / | / | / | / | / | / | /
902 | 44 | 南非 | 00 | SA | 南非 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.5 | 52 | 50 | 0 | 4000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.5 | 52 | 50 | 0 | 4000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[15 empty] | 0 | 0 |  |  |  | 0 | 0
902 |  | 南非 | 01 | SA-HV | 南非-高压 | [9 empty] | 0 | 0 |  |  |  | 0 | 0
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.5 | 52 | Droop 0~10%可调 | 0 | / | 50.2 |  | / | / | / | / | / | / | / | / | / |  |  |  | 0 | / |  |  | / | / | / | / | / | / | / | / | /
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.5 | 52 | 10 | 0 | 4000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.5 | 52 | 50 | 0 | 4000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 45 | [13 empty] | 0 | 0 |  |  |  | 0 | 0 | 50.2 | 52 | 40 | 0 |  | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 |  | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
[5 empty] | 迪拜安规标准 | 1kV以下 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4129 | 50.3Hz | 52.5 | 45.45%P/Hz | / | ≥300s | 50.1Hz | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | [9 empty] | 50.3Hz |  | 45.45%P/Hz | / | ≥300s | 50.1Hz | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute)
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4129 | 50.3 | 52.5 | 45 | 0 | 310000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.1 | 49.85 | 50.3 | 52 | 45 | 0 | 310000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.1 | 49.85 | 51 | 49
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4129 | 50.3Hz | 52.5 | 45.45%P/Hz |  | ≥300s | 50.1Hz | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute) | [9 empty] | 50.3Hz |  | 45.45%P/Hz |  | ≥300s | 50.1Hz | ≤20% (≤20%PMEM/minute ≥5%Pnom/minute)
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 1 | 1 | 0 | 0 | 4129 | 50.3 | 52.5 | 45 | 0 | 310000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.1 | 49.85 | 50.3 | 52 | 45 | 0 | 310000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.1 | 49.85 | 51 | 49
902 | 47-106 | [13 empty] | 0 | 0 |  |  |  | 0 | 0 | 50.2 | 52 | 40 | 0 |  | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 |  | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2Hz | / | 40%PN/Hz | / | / | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | / | / | [7 empty] | 50.2Hz | / | 40%PN/Hz | / | / | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | / | /
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2Hz | / | 40%PN/Hz | / | / | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | / | / | [7 empty] | 50.2Hz | / | 40%PN/Hz | / | / | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10% | / | /
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 8 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 8 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 110 | [13 empty] | 0 | 0 | 0 |  |  | 0 | 0
[5 empty] | 哥伦比亚安规标准 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 40 | 0 | 60000 | 50 | 9 | 49.5 | 48.5 | 40 | 0 | 2000 | 50 | 17 | 50.2 | 47.5 | 50 | 52 | 40 | 0 | 60000 | 50 | 9 | 49.5 | 48.5 | 40 | 0 | 2000 | 50 | 17 | 50.2 | 47.5 | 51 | 49
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 40 | 0 | 60000 | 50 | 9 | 49.5 | 48.5 | 40 | 0 | 2000 | 50 | 17 | 50.2 | 47.5 | 50 | 52 | 40 | 0 | 60000 | 50 | 9 | 49.5 | 48.5 | 40 | 0 | 2000 | 50 | 17 | 50.2 | 47.5 | 51 | 49
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 112 | 智利 | 00 | Chile | 智利 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 52 | 40 | 0 | 60000 | 50 | 9 | 49.5 | 48.5 | 40 | 0 | 2000 | 50 | 17 | 50.2 | 47.5 | 50 | 52 | 40 | 0 | 60000 | 50 | 9 | 49.5 | 48.5 | 40 | 0 | 2000 | 50 | 17 | 50.2 | 47.5 | 51 | 49
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.2 | 62.5 | 53 | 0 | 60000 | 60 | 9 | 59.5 | 58.5 | 40 | 0 | 2000 | 60 | 17 | 60.5 | 58.8 | 60.2 | 62.5 | 53 | 0 | 60000 | 60 | 9 | 59.5 | 58.5 | 40 | 0 | 2000 | 60 | 17 | 60.5 | 58.8 | 61 | 59
|  |  |  | 客户需求参考EU-EN50549 | [10 empty] | 0 | 0 |  |  |  | 0
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | 客户需求参考EU-EN50549 | [6 empty] | 0 | 0 | 1 |  | 0 | 0 |  |  |  | 0 | [5 empty] | 0-600000(建议大于30000ms) | 50.1
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 1 | 0 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 1000 | 50.2 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49
|  |  |  | AnnexC_EN 50549-2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.2Hz-52Hz（默认50.5Hz) | 52 | 16.67%Pn/Hz-100%Pn/Hz（默认50%Pn/Hz） | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | 49.8Hz-46Hz(默认49.8Hz) | / | 16.67%Pn/Hz-100%Pn/Hz（默认40%Pn/Hz） | / | / | / | / | / | / | 50.2 | 52 | 40 | 0-2000 | 0-600000 | 当频率减小时，逆变器输出功率相应增大，随频率相应变化,如果频率恢复到50Hz,但是功率还不能达到最大时，此时功率按照<10%进行恢复 | <10 | / | / | / | / | / | / | / | / | /
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.5 | 52 | 50 | 0 | 35000 | 50.1 | 9 | 49.8 | 48 | 40 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 50.2 | 52 | 40 | 0 | 35000 | 50.1 | 9 | 49.75 | 48 | 57 | 0 | 30000 | 49.85 | 17 | 50.2 | 49.85 | 51 | 49

## 无功参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | Bit0：无功使能 | Bit1-3：无功模式 （不需要填写） | Bit1 | Bit2 | Bit3 | Bit8：无功模式三电压进入使能位 | Bit9：充电无功使能 | Bit10：按最大相电压控制使能位 | ReactiveConfig 总使能位（自动生成） | PowerFactor | FixedReactivePercentage | ReactiveCos1 | ReactivedynamicValue1 | ReactiveCos2 | ReactivedynamicValue2 | ReactiveCos3 | ReactivedynamicValue3 | ReactiveCos4 | ReactivedynamicValue4 | LockinV | LockoutV | HighVoltStartValue4 | HighVoltEndValue4 | LowVoltStartValue4 | LowVoltEndValue4 | LockinPower4 | LockoutPower4 | MaxLeadingReactivePower4 | ReactiveResponseWaitTime4 | ReactivePowerOffset4 | ReactivePowerStart4 | HighVoltStartValue5 | HighVoltEndValue5 | LowVoltStartValue5 | LowVoltEndValue5 | LockinPower5 | LockoutPower5 | MaxReactivePower5 | ReactiveResponseWaitTime5 | PhaseType | ReactiveResponsePeriod | MaxLaggingReactivePower4
[15 empty] | Bit0：无功使能 Bit1-3：无功模式 Bit8：无功模式三电压进入使能位 Bit9：充电无功使能 Bit10：无功模式四奥地利使能位 | 功率因数，用于无功模式一计算Tanphi | 固定无功功率百分比，用于无功模式二计算无功量 | 用于无功模式三，第一点功率因数值 | 用于无功模式三，第一点功率百分比 | 用于无功模式三，第二点功率因数值 | 用于无功模式三，第二点功率百分比 | 用于无功模式三，第三点功率因数值 | 用于无功模式三，第三点功率百分比 | 用于无功模式三，第四点功率因数值 | 用于无功模式三，第四点功率百分比 | 用于无功模式三，LockinV电压数值百分比 | 用于无功模式三，LockoutV电压数值百分比 | 用于无功模式四，高压起始电压百分比 | 用于无功模式四，高压终止电压百分比 | 用于无功模式四，低压起始电压百分比 | 用于无功模式四，低压终止电压百分比 | 用于无功模式四，Lockin功率值百分比 | 用于无功模式四，Lockout功率值百分比 | 用于无功模式四，最大超前无功功率百分比 | 用于无功模式四，无功响应等待时间 | 用于无功模式四，无功功率偏移量百分比。在整个运行电压范围内偏移无功曲线。正值表示超前，负值表示滞后。 | 用于无功模式四，低压起始电压至高压起始电压点无功功率变化范围百分比的50%。低压起始电压对应该寄存器滞后的无功功率；高压起始电压对应该寄存器超前的无功功率； | 用于无功模式五，高压起始电压百分比 | 用于无功模式五，高压终止电压百分比 | 用于无功模式五，低压起始电压百分比 | 用于无功模式五，低压终止电压百分比 | 用于无功模式五，Lockin功率值百分比 | 用于无功模式五，Lockout功率值百分比 | 用于无功模式五，最大无功功率百分比 | 用于无功模式五，无功响应等待时间 | 用于无功模式六，相位类型 0：零无功功率 1：滞后无功功率 2：超前无功功率 | 用于无功（1、2、3、4、5、6）设置无功调节时长 | 无功模式四，最大滞后无功功率百分比
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [9 empty] | 0.0001 | 0.01 | 0.0001 | 1 | 0.0001 | 1 | 0.0001 | 1 | 0.0001 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.01 | 10 | 0.01 | 0.01 | 1 | 1 | 1 | 1 | 1 | 1 | 0.01 | 10 |  | 1 | 0.01
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [10 empty] | % |  | % |  | % |  | % |  | % | % | % | % | % | % | % | % | % | %Pn | ms | %Qmax | %Pn | % | % | % | % | % | % | % | ms |  | 秒 | %Pn
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 1 | 4 | 1 | 1 |  |  |  |  | 7 | [9 empty] | %: 103; %: 107; %: 97; %: 93; %Pn: 48.43% |  |  | 48.43%
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 103 | 107 | 97 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 48.43
[6 empty] | 旧4110标准 | 0 | 4 | 1 | 1 |  |  |  |  | 6 | [9 empty] | %: 104; %: 0; %: 96; %Pn: 60 |  |  | 60
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 0 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 6 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 104 | 104 | 0 | 96 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 60
[6 empty] | 德国该标准已撤销 | 1 | 4 | 1 | 1 |  |  |  | 0 | 7 | [9 empty] | %Pn: 48.43 |  |  | 48.43
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 0 | [7 empty] | 0 | [9 empty] | %: 100; %: 104; %: 100; %: 96; %Pn: 60 |  |  | 60
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 100 | 104 | 100 | 96 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 60
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 0 | [7 empty] | 0 | [9 empty] | %: 100; %: 104; %: 100; %: 96; %Pn: 60 |  |  | 60
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 100 | 104 | 100 | 96 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 60
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 1 | 4 | 1 | 1 |  |  |  |  | 7 | [9 empty] | %: 108; %: 110; %: 92; %: 90; %: 20; %: 5; %Pn: 48.43
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[6 empty] | 1、正标 2、系统电压≤1KV | 1 | 4 | 1 | 1 |  |  |  |  | 7 | [9 empty] | %: 108; %: 110; %: 92; %: 90; %: 20; %: 5; %Pn: 48.43; ms: 0-30S（默认设置3S）
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 3000 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 1 | 4 | 1 | 1 |  |  |  |  | 7 | [9 empty] | %: 108; %: 110; %: 92; %: 90; %: 20; %: 5; %Pn: 48.43
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 1 | 4 | 1 | 1 |  |  |  |  | 7
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压
[7 empty] | 1 | 4 | 1 | 1 |  |  |  |  | 7 | [9 empty] | %: 108; %: 110; %: 92; %: 90; %: 20; %: 5; %Pn: 48.43
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[7 empty] | 1 | 4 | 1 | 1 |  |  |  |  | 7 | [9 empty] | %: 108; %: 110; %: 92; %: 90; %: 20; %: 5; %Pn: 48.43
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 1 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 519 | / | / | / | / | / | / | / | / | / | / | / | / | 240V | 258V | 220V | 207V | 0 | 0 | 60 | / | / | / | / | / | / | / | / | / | / | / | / | / | 44
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 1 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 519 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 44
|  |  |  | ASNZS4777.2-2020 | / |  |  | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 518 | / | / | / | / | / | / | / | / | / | / | / | / | 235V | 255V | 220V | 205V | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | 0 | 30
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 1 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 519 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 102 | 110 | 95 | 89 | 0 | 0 | 40 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 30
|  |  |  | ASNZS4777.2-2020 | / |  |  | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 518 | / | / | / | / | / | / | / | / | / | / | / | / | 240V | 255V | 230V | 215V | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | 0 | 44
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 1 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 519 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 111 | 100 | 93 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 44
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | 100 | 107 | 100 | 93 | / | / | 30 | / | / | / | / | / | / | / | / | / | / | / | / | / | 30
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 100 | 107 | 100 | 93 | 0 | 0 | 30 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 30
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | Spain island | 西班牙island |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[6 empty] | 非标低压安规文件 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | VDE0126(Greece Continent) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | VDE0126(Greece island) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | EU-EN50549-1 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压
|  |  |  | C10/11 | 比利时 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压
[6 empty] | 非标低压安规文件 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | UK-G99标准 |  |  | 0 |  | / | / | / | 0 | 0 | 0 |  | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | UK-G98标准 |  |  | 0 |  | / | / | / | 0 | 0 | 0 |  | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 00 | China | 中国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | CNS+15382-2018 |  |  | 1 | / | / | / | / | 1 | 0 | 0 |  | / | / | 0.9 | 0 | 0.9 | 50 | 0.9 | 100 | 0.39 | / | 105 | 104 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | /
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 1 | 3 | 0 | 1 | 0 | 1 | 0 | 0 | 261 | 1 | 100 | 0.9 | 0 | 0.9 | 50 | 0.9 | 100 | 0.9 | 200 | 105 | 104 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | NB/T 32004-2018 |  |  | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 中国 | 07 | China-MV | 中国-中压
902 |  | 中国 | 08 | China-HV | 中国-高压
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 09 | China | 中国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 中国CQC B类 |  | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[7 empty] | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 中国CQC B类 |  | / | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | / | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | /
902 | 11 | 法国 | 00 | France | 法国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | FRArrete23 | 法国Arrete23 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | / | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | /
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | France | 法国VDE0126 | Enedis客户 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.943 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.943 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.943 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.943 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.94 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.94 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.94 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | [9 empty] | %: 106Un; %: 108Un; %: 94Un; %: 92Un; %: 20%Pn; %: 5%Pn; %Pn: 48.43 |  |  | 48.43
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 106 | 108 | 94 | 92 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | [9 empty] | %: 106Un; %: 108Un; %: 94Un; %: 92Un; %: 20%Pn; %: 5%Pn; %Pn: 48.43 |  |  | 48.43
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 106 | 108 | 94 | 92 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1025 | 1 | / | / | / | / | / | / | / | / | / | / | / | 105 | 108 | 96 | 92 | 0 | 0 | 43.6%Sn | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | 10 | 43.6%Sn
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1025 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 96 | 92 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 43.6
902 | 14 | 日本 | 00 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
0
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 103 | 107 | 97 | 93 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 43.6
0
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 0 | 0 | 103 | 107 | 97 | 93 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 43.6
902 | 16-17 | [13 empty] | 0
[6 empty] | 被 EN50549替代 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | EU-EN50549-1 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 欧洲-IEC EN61727 |  | / | / | / | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | / | / |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 101 | 105 | 99 | 95 | 0 | 0 | 48.4 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.4
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 101 | 105 | 99 | 95 | 0 | 0 | 48.4 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.4
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | EN50549-1 | / |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压
902 | 23 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[7 empty] | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 100 | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 100 | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 1 | 3(默认使能无功模式三） | 0 | 1 |  | 0 | 0 | 0 | 5 |  |  | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | %: 100; %: 105; %: 100; %: 103; %: 107; %: 97; %: 93; %Pn: 48.43 |  |  | 48.43
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 100 | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | 100 | 105 | 100 | 103 | 107 | 97 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 3(默认使能无功模式三） | 0 | 1 |  | 0 | 0 | 0 | 5 |  |  | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | %: 100; %: 105; %: 100; %: 103; %: 107; %: 97; %: 93; %Pn: 48.43 |  |  | 48.43
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 100 | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | 100 | 105 | 100 | 103 | 107 | 97 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 3(默认使能无功模式三） | 0 | 1 |  | 0 | 0 | 0 | 5 |  |  | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | %: 100; %: 105; %: 100; %: 100; %: 104; %: 100; %: 96; %Pn: 48.43 |  |  | 48.43
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 1 | 100 | 1 | 10 | 1 | 20 | 1 | 40 | 0.9 | 100 | 105 | 100 | 100 | 104 | 100 | 96 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | IEC61727 | 印度-IEC61727 |  | / | / | / | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 25 | 印度 | 00 | India | 印度 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 印度 | 01 | India-MV | 印度-中压
902 |  | 印度 | 02 | India-HV | 印度-高压
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | / | / | / | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[6 empty] | Kerala地区安规参数 | / | / | / | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | [8 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压
[7 empty] | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 256 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 519 | / | / | / | / | / | / | / | / | / | / | / | / | 235V | 244V | 220V | 207V | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | 0 | 60
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 1 | 4 | 1 | 1 | 0 | 0 | 1 | 0 | 519 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 102 | 106 | 95 | 90 | 0 | 0 | 60 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 60
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 256 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 256 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 256 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 256 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288
[5 empty] | 斯洛伐克VSD测试设定值 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 斯洛伐克SSE测试设定值 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  | 捷克 |  |  | 捷克（中压） |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | Czechia | 捷克<=16A系统 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | Czechia | 捷克>16A系统 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 20 | 48.43
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 97 | 94 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 48.43
[7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 | 32
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 挪威 | 00 | Norway | 挪威 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 34 | 挪威低压 | 01 | Norway-LV | 挪威低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 墨西哥低压测试设定值 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 36-37 | [13 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[6 empty] | ＞25A/16A | 0 | [7 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 0 | [7 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[7 empty] | 0 |  | / | / | / | 0 | 0 | 0 |  | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[7 empty] | 0 |  | / | / | / | 0 | 0 | 0 |  | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 泰国PEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 大于500KW系统，需开启QU | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | 108%Un | 110%Un | 92%Un | 90%Un | 20%Pn | 5%Pn | 48.43%Pn | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43%Pn
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 泰国MEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | 108%Un | 110%Un | 92%Un | 90%Un | 20%Pn | 5%Pn | 48.43%Pn | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43%Pn
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 108 | 110 | 92 | 90 | 20 | 5 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 | 41 | [13 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 43 | [13 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 0 | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 44 | 南非 | 00 | SA | 南非 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 |  | 南非 | 01 | SA-HV | 南非-高压
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | 0 | / | / | / | / | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 45 | [13 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
[5 empty] | 迪拜安规标准 | 1kV以下 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43 | / | / | / | / | / | / | / | / | / | / | / | / | / | 48.43
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 43.6 | / | / | / | / | / | / | / | / | / | / | / | / | / | 43.6
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 47-106 | [13 empty] | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | / | / | / | / | / | / | / | / | / | / | / | / | 105 | 108 | 96 | 92 | / | / | 43.6 | / | / | / | / | / | / | / | / | / | / | / | / | 1 | 43.6
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 1 | 4 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 105 | 108 | 96 | 92 | 0 | 0 | 43.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
902 | 110 | [6 empty] | 1 | [6 empty] | 0
[5 empty] | 哥伦比亚安规标准 |  | 0 | [7 empty] | 0 | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 103 | 107 | 97 | 93 | 20 | 5 | 44 | 2000 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 65535
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 103 | 107 | 97 | 93 | 20 | 5 | 44 | 2000 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 65535
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | / | / | / | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | [21 empty] | / | / | / | bar: % to ms
902 | 112 | 智利 | 00 | Chile | 智利 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 103 | 107 | 97 | 93 | 20 | 5 | 44 | 2000 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 43.6
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 50 | 1 | 50 | 1 | 50 | 0.95 | 100 | 105 | 100 | 105 | 110 | 95 | 90 | 0 | 0 | 43.6 | 2000 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 43.6
客户需求参考EU-EN50549
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | 客户需求参考EU-EN50549 | [20 empty] | %Pn: 48.43 |  |  | 48.43
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 112 | 95 | 90 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 43.6
|  |  |  | AnnexC_EN 50549-2 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0-20 | 0-20 | 48.43 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | 1 | 48.43
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 50 | 1 | 50 | 1 | 50 | 0.9 | 100 | 105 | 100 | 104 | 107 | 96 | 93 | 0 | 0 | 48.43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 48.43

## 电压穿越参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | Bit0：LVRT使能位 | Bit1：OVRT使能位 | Bit2：零电流模式使能位 | Bit3：继承穿越前无功电流 | Bit4：使用跌落前的电压计算电流 | Bit5：负序电流使能位 | Bit6:高穿有功使能位 | Bit7：低穿有功使能位 | Bit8-11：电压穿越电流计算模式 （不需要计算） | Bit8：电压穿越电流计算模式(0：无效；1: 德国4110计算模式) | Bit9：电压穿越电流计算模式 | Bit10：电压穿越电流计算模式 | Bit11：电压穿越电流计算模式 | VRTConfig 总使能位（自动生成） | LvrtInVolt | LvrtFirstPointVolt | LvrtFirstPointTime | LvrtSecondPointVolt | LvrtSecondPointTime | LvrtThirdPointVolt | LvrtThirdPointTime | LvrtFourthPointVolt | LvrtFourthPointTime | LvrtReactiveCurrentCoefficientK | LvrtWaitingTimeAfterVoltageRecovery | LvrtPowerBackRate | OvrtInVlot | OvrtFirstPointVolt | OvrtFirstPointTime | OvrtSecondPointVolt | OvrtSecondPointTime | OvrtThirdPointVolt | OvrtThirdPointTime | OvrtFourthPointVolt | OvrtFourthPointTime | OvrtReactiveCurrentCoefficientK | OvrtWaitingTimeAfterVoltageRecovery | OvrtPowerBackRate | ZeroCurrentModeInLowVolt | ZeroCurrentModeInHighVolt | LvrtOutVolt | LvrtIqVoltStart | OvrtOutVolt | OvrtIqVoltStart | MaxUnbalanceIqPct | OVRTActivePowerVoltMin | LVRTActivePowerVoltMin
[20 empty] | Bit0：LVRT使能位 Bit1：OVRT使能位 Bit2：零电流模式使能位 Bit3：继承穿越前无功电流 Bit4：使用跌落前的电压计算电流 Bit5：负序电流使能位 Bit8-11：电压穿越电流计算模式 | 进入LVRT电压值百分比 | 低压穿越第一点电压百分比 | 低压穿越第一点时间 | 低压穿越第二点电压百分比 | 低压穿越第二点时间 | 低压穿越第三点电压百分比 | 低压穿越第三点时间 | 低压穿越第四点电压百分比 | 低压穿越第四点时间 | 低压穿越无功电流系数K | 低压穿越恢复后的等待时间 | 低压穿越功率回载速率 | 进入OVRT电压值百分比 | 高压穿越第一点电压百分比 | 高压穿越第一点时间 | 高压穿越第二点电压百分比 | 高压穿越第二点时间 | 高压穿越第三点电压百分比 | 高压穿越第三点时间 | 高压穿越第四点电压百分比 | 高压穿越第四点时间 | 高压穿越无功电流系数K | 高压穿越恢复后的等待时间 | 高压穿越功率回载速率 | 零电流模式进入低电压百分比 | 零电流模式进入高电压百分比 | 低压穿越退出电压值百分比 | 低压穿越无功电流计算起始电压值百分比 | 高压穿越退出电压值百分比 | 高压穿越无功电流计算起始电压值百分比 | 不平衡穿越最大无功电流百分比 | 高穿有功功率起始电压值百分比 | 低穿有功功率起始电压值百分比
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [14 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.1 | 1 | 1 | 1 | 1 | 10 | 1 | 10 | 1 | 10 | 1 | 10 | 0.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [14 empty] | % | % | ms | % | ms | % | ms | % | ms | p.u. | ms | %Pn/min | % | % | ms | % | ms | % | ms | % | ms | p.u. | ms | %Pn/min | % | % | % | % | % | % | % | % | %
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 1 | 1 |  |  |  | 1 | 0 | 0 | [5 empty] | 35 | 80 | 15 | 150 | 25 | 500 | 50 | 1500 | 80 | ≥60000 |  |  | ＜200ms恢复到90%Pn以上 | 115 | 125 | ≥100 | 120 | ≥5000 | 115 | ≥60000 | 115 | ≥60000 | [5 empty] | 81 | 80 | 114 |  | 100 | 100 | 70
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 80 | 15 | 220 | 25 | 640 | 50 | 1640 | 80 | 60100 | 0 | 0 | 30000 | 115 | 125 | 160 | 120 | 5100 | 115 | 60100 | 115 | 60100 | 0 | 0 | 30000 | 50 | 120 | 81 | 80 | 114 | 115 | 100 | 100 | 70
[6 empty] | 旧4110标准 | 1 | 1 |  | 1 |  | 1 | 0 | 0 | [5 empty] | 43 | 90 | 0-5 | ＞318 | 20-30 | ＞1332 | 45-60 | ＞2305 | 85-90 | ≥60000 | 2 |  | ＜200ms恢复到90%Pn以上 | 110 | 125 | ≥100 | 120 | ≥5000 | 115 | ≥60000 | 110 | ≥60000 | 2 |  |  |  |  | 91 | 100 | 109 | 100 | 100 | 100 | 70
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 90 | 3 | 330 | 25 | 1450 | 50 | 2500 | 90 | 60100 | 2 | 0 | 30000 | 110 | 125 | 160 | 120 | 5100 | 115 | 60100 | 110 | 60100 | 2 | 0 | 30000 | 50 | 120 | 91 | 100 | 109 | 100 | 100 | 100 | 70
[6 empty] | 德国该标准已撤销 | 0 | 0 |  |  |  |  | 0 | 0 | [5 empty] | 0 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  |  | 507 | 90 | 20-30 | ＞1332 | 45-60 | ＞2305 | 70-80 | ＞3000 | 85-90 | ＞60000 | 2 |  | ＜200ms恢复到90%Pn以上 | 110 | 125 | ≥100 | 120 | ≥5000 | 115 | ＞5000 | 110 | ＞60000 | 2 |  |  |  |  | 91 | 90%Un | 109 | 110%Un | 100 | 100 | 70
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 507 | 90 | 25 | 1450 | 50 | 2500 | 75 | 3100 | 90 | 60100 | 2 | 0 | 30000 | 110 | 125 | 160 | 120 | 5100 | 115 | 5100 | 110 | 60100 | 2 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 1 | 1 |  | 1 | 1 | 1 | 0 | 0 | [5 empty] | 59 | 90 | 0-5 | ＞406 | 20-30 | ＞1332 | 45-60 | ＞2444 | 70-80 | ＞3000 | 2 |  | ＜200ms恢复到90%Pn以上 | 110 | 125 | ≥100 | 120 | ≥5000 | 115 | ＞5000 | 110 | ＞60000 | 2 |  |  |  |  | 91 | 90%Un | 109 | 110%Un | 100 | 100 | 70
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 90 | 3 | 420 | 25 | 1450 | 50 | 2500 | 75 | 3100 | 2 | 0 | 30000 | 110 | 125 | 160 | 120 | 5100 | 115 | 5100 | 110 | 60100 | 2 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 1 | 1 |  |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[6 empty] | 1、正标 2、系统电压≤1KV | 1 | 1 |  |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 10 | 200 | 25 | 400 | 50 | 850 | 75 | 1300 | 0 | 0 | 30000 | 110 | 125 | 100 | 120 | 5000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | CEI-021Ex. | 意大利(0-21)外部 | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 1 | 0 |  |  |  |  | 0 | 0 | [5 empty] | 1 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 85 | 10 | 200 | 25 | 400 | 50 | 850 | 75 | 1300 | 0 | 0 | 30000 | 110 | 125 | 100 | 120 | 5000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 0 | 0 |  |  |  |  | 0 | 0 | [5 empty] | 0 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[14 empty] | 0 | [37 empty] | 100 | 70
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压 | [8 empty] | 0 | [37 empty] | 100 | 70
[7 empty] | 1 | 1 |  |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 10 | 200 | 25 | 400 | 50 | 850 | 75 | 1300 | 0 | 0 | 30000 | 110 | 125 | 100 | 120 | 5000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[7 empty] | 1 | 1 |  |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 10 | 200 | 25 | 400 | 50 | 850 | 75 | 1300 | 0 | 0 | 30000 | 110 | 125 | 100 | 120 | 5000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | ASNZS4777.2-2020 | 澳大利亚 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | 180V | 260V | 86 | / | 109 | / | 100 | 100 | 70
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 78 | 113 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | ASNZS4777.2-2020 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | 180V | 260V | 86 | / | 109 | / | 100 | 100 | 70
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 78 | 113 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | ASNZS4777.2-2020 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | 180V | 260V | 86 | / | 109 | / | 100 | 100 | 70
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 78 | 113 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 185 | / | / | / | / | / | / | / | / | / | 3.5 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 185 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 3.5 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | Spain island | 西班牙island |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[6 empty] | 非标低压安规文件 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 43.6 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 10 | ≥250 | 40 | ≥750 | 70 | ≥1250 | / | / | / | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 51 | / | 119 | / | 100 | 100 | 70
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 43.6 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 85 | 119 | 115 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 |  | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 |  | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | VDE0126(Greece Continent) |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | VDE0126(Greece island) |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | C10/11 | 比利时 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 75 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 115 | ≥60000 | / | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 5 | 440 | 25 | 1040 | 50 | 1890 | 75 | 3090 | 0 | 0 | 30000 | 120 | 125 | 160 | 120 | 5090 | 115 | 60090 | 115 | 60090 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[6 empty] | 非标低压安规文件 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 75 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 115 | ≥60000 | / | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 5 | 440 | 25 | 1040 | 50 | 1890 | 75 | 3090 | 0 | 0 | 30000 | 120 | 125 | 160 | 120 | 5090 | 115 | 60090 | 115 | 60090 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | UK-G99标准 |  |  | 1 | 1 | 0 | 0 | 0 | / | 0 | 0 |  | / | / | / | / |  | 90 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | UK-G98标准 |  |  | 1 | 1 | 0 | 0 | 0 | / | 0 | 0 |  | / | / | / | / |  | 90 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 0 | 0 | 0 | / | / | / | 1 | 0 |  | / | / | / | / |  | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | / | / | / | / | / | 110 | 130 | 500 | 120 | 10000 | / | / | / | / |  |  | / |  |  |  |  | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 00 | China | 中国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | CNS+15382-2018 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | NB/T 32004-2018 |  |  | 0 | 0 | 0 | / | / | / | 0 | 0 |  | / | / | / | / |  | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | / | / | / | / | / | 110 | 130 | 500 | 120 | 10000 | / | / | / | / |  |  | / |  |  |  |  | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[7 empty] | 1 | 1 |  |  |  |  | 0 | 0 | [34 empty] | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [34 empty] | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 0 | 0 | 0 | / | / | / | 0 | 0 |  | / | / | / | / |  | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | / | / | / | / | / | 110 | 130 | 500 | 120 | 10000 | / | / | / | / |  |  | / |  |  |  |  | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [34 empty] | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 中国 | 07 | China-MV | 中国-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 中国 | 08 | China-HV | 中国-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | 1 | 1 | / | / | / | / | 1 | 0 |  | / | / | / | / |  | 90 | 0 | ≥150 | 20 | ≥625 | / | / | 90 | ≥2000 | 1.5-2.5（默认设置1.5） | / | / | 110 | 130 | ≥500 | 120 | ≥10000 | / | / | 110 | 连续运行 | 0-1.5（默认设置1.5） | / | / |  |  | 91 | 90 | 109 | 110 | 100 | 100 | 70
902 | 10 | 中国 | 09 | China | 中国 |  | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 90 | 0 | 400 | 20 | 1000 | 50 | 1850 | 90 | 3000 | 1.5 | 0 | 30000 | 110 | 130 | 550 | 120 | 10100 | 115 | 60050 | 110 | 60100 | 1.5 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
[5 empty] | 中国CQC B类 |  | 0 | 0 | 0 | / | / | / | 0 | 0 |  | / | / | / | / |  | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | / | / | / | / | / | 110 | 130 | 500 | 120 | 10000 | / | / | / | / |  |  | / |  |  |  |  | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[7 empty] | 0 | 0 | 0 | / | / | / | 0 | 0 |  | / | / | / | / |  | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | / | / | / | / | / | 110 | 130 | 500 | 120 | 10000 | / | / | / | / |  |  | / |  |  |  |  | 109 |  | 100 | 100 | 70
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 中国CQC B类 |  | 0 | 0 | 0 | / | / | / | 1 | 0 |  | / | / | / | / |  | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | / | / | / | / | / | 110 | 130 | 500 | 120 | 10000 | / | / | / | / |  |  | / |  |  |  |  | 109 |  | 100
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 150 | 20 | 625 | 90 | 2000 | 90 | 3000 | 1.5 | 0 | 30000 | 110 | 130 | 500 | 120 | 10000 | 115 | 60050 | 110 | 60100 | 1.5 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 11 | 法国 | 00 | France | 法国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | FRArrete23 | 法国Arrete23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | France | 法国VDE0126 | Enedis客户 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[14 empty] | 0 | [37 empty] | 100 | 70
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis | [8 empty] | 0 | [37 empty] | 100 | 70
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 1 |  | 1 | 1 | 1 | 0 | 0 | [5 empty] | 59 | 90 | 0-5 | ＞406 | 20-30 | ＞1332 | 45-60 | ＞2444 | 70-80 | ＞3000 | 2 |  | ＜200ms恢复到90%Pn以上 | 110 | 125 | ≥100 | 120 | ≥5000 | 115 | ＞5000 | 110 | ＞60000 | 2 |  |  |  |  | 91 | 90 | 109 | 110 | 100 | 100 | 70
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 90 | 3 | 420 | 25 | 1450 | 50 | 2500 | 75 | 3100 | 2 | 0 | 30000 | 110 | 125 | 160 | 120 | 5100 | 115 | 5100 | 110 | 60100 | 2 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0-5 | ≥150～≥290 | 15-25 | ≥570～≥850 | 45-55 | ≥1400～≥1700 | 65-75 | ≥1950～≥2250 | [21 empty] | 100 | 100 | 70
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 90 | 0-5 | ≥150～≥290 | 15-25 | ≥570～≥850 | 45-55 | ≥1400～≥1700 | 85Un | ≥3000ms | 2 |  |  | 110Un | 125Un | ≥100ms | 120Un | ≥5000ms | 115Un | ≥60000ms |  |  | 2 |  |  | 80Un | 115Un | 91Un | 90Un | 109Un | 110Un | 100 | 100 | 70
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 90 | 4 | 400 | 25 | 1000 | 50 | 1850 | 85 | 3000 | 2 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 2 | 0 | 30000 | 80 | 115 | 91 | 90 | 109 | 110 | 100 | 100 | 70
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 5 | 50 | 15 | ≥150ms | 50 | ≥840ms |  |  | 50 | ≥60000ms |  |  |  | 120 |  |  |  |  | 120 |  | 120 |  |  |  |  | 80%Un | 115%Un | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 15 | 200 | 50 | 900 | 50 | 1000 | 50 | 60050 | 0 | 0 | 30000 | 120 | 125 | 160 | 120 | 5090 | 120 | 60090 | 120 | 60090 | 0 | 0 | 30000 | 80 | 115 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 14 | 日本 | 00 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [34 empty] | 109 |  | 100 | 100 | 70
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [34 empty] | 109 |  | 100 | 100 | 70
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 16-17 | [11 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[6 empty] | 被 EN50549替代 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  | 欧洲通用 |  | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 |  | 1 |  |  |  | 507 | 90 | 0-5 | ＞406 | 20-30 | ＞1332 | 45-60 | ＞2444 | 70-80 | ＞3000 | 2 |  | ＜200ms恢复到90%Pn以上 | 110 | 125 | ≥100 | 120 | ≥5000 | 115 | ＞5000 | 110 | ＞60000 | 2 |  |  |  |  | 91 | 90 | 109 | 110 | 100 | 100 | 70
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 507 | 90 | 3 | 420 | 25 | 1450 | 50 | 2500 | 75 | 3100 | 2 | 0 | 30000 | 110 | 125 | 160 | 120 | 5100 | 115 | 5100 | 110 | 60100 | 2 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
|  |  |  | IEC EN61727 | 欧洲-IEC EN61727 |  | / | / | / | / | / | / | 0 | 0 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | / | / |  | / | / | / | / | / | / | 0 | 0 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 300 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 300 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | EN50549-1 | / |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 | 23 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 0 | 0 |  |  |  |  | 0 | [6 empty] | 0 | 80 | 15 | 150 | 25 | 500 | 50 | 1500 | 80 | ≥60000 | 0 |  | ＜200ms恢复到90%Pn以上 | 115 | 125 | ≥100 | 120 | ≥5000 | 115 | ≥60000 | 115 | ≥60000 | [5 empty] | 81 | 80 | 114 | 115 | 100
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 150 | 25 | 500 | 50 | 1500 | 80 | 60500 | 0 | 0 | 30000 | 115 | 125 | 120 | 120 | 5050 | 115 | 60050 | 115 | 60050 | 0 | 0 | 30000 | 50 | 120 | 81 | 80 | 114 | 115 | 100 | 100 | 70
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 1 |  |  |  |  | 0 | [6 empty] | 3 | 90 | 15 | 150 | 25 | 330 | 50 | 780 | 90 | 1500 | 0 |  | ＜200ms恢复到90%Pn以上 | 115 | 125 | ≥100 | 120 | ≥5000 | 115 | ≥60000 | 115 | ≥60000 | [5 empty] | 91 | 90 | 114 | 115 | 100
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 15 | 150 | 25 | 330 | 50 | 780 | 90 | 1500 | 0 | 0 | 30000 | 115 | 125 | 120 | 120 | 5050 | 115 | 60050 | 115 | 60050 | 0 | 0 | 30000 | 50 | 120 | 91 | 90 | 114 | 115 | 100 | 100 | 70
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 1 |  | 1 | 1 | 1 | 0 | [6 empty] | 59 | 90 | 15 | 150 | 25 | 330 | 50 | 780 | 90 | 1500 | 2 |  | ＜200ms恢复到90%Pn以上 | 110 | 125 | ≥100 | 120 | ≥5000 | 115 | ＞5000 | 110 | ＞60000 | 2 |  |  |  |  | 91 | 90%Un | 109 | 110%Un | 100
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 90 | 15 | 150 | 25 | 330 | 50 | 780 | 90 | 1500 | 2 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 5050 | 110 | 60050 | 2 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
|  |  |  | IEC61727 | 印度-IEC61727 |  | / | / | / | / | / | / | 0 | 0 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 25 | 印度 | 00 | India | 印度 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 印度 | 01 | India-MV | 印度-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 印度 | 02 | India-HV | 印度-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 90 | 15 | 400 | 25 | 740 | 50 | 1700 | 90 | 11100 | 1 | 0 | 30000 | 111 | 130＜V(建议值132） | 20 | 130≥V＞120（建议值130） | ＞0.2s（建议值240） | 120≥V＞110（建议值115） | ＞2s（建议值2100） | 115 | 2100 | 0 | 0 | 30000 | 50 | 120 | 91 | 100 | 110 | 111 | 100 | 100 | 70
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 15 | 400 | 25 | 740 | 50 | 1700 | 90 | 11100 | 1 | 0 | 30000 | 111 | 132 | 20 | 130 | 240 | 115 | 2100 | 115 | 2100 | 0 | 0 | 30000 | 50 | 120 | 91 | 100 | 110 | 111 | 100 | 100 | 70
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | / | / | / | / | / | / | 0 | 0 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[6 empty] | Kerala地区安规参数 | / | / | / | / | / | / | 0 | 0 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. | 0 | 1 |  |  |  |  | 0 | 0 | [5 empty] | 2 | 90 | 0 | ≧150 | 20 | ≧625 | 50 | ≧1643 | 90 | ≧3000 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 90 | 0 | 400 | 20 | 1000 | 50 | 1850 | 90 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[7 empty] | 0 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 86 | / | 109 | / | 100 | 100 | 70
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | ASNZS4777.2-2020 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 0 | / | / | 180V | 260V | 86 | / | 109 | / | 100 | 100 | 70
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 78 | 113 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | ≥6KW系统开启 | 0 | 0 |  |  |  | 0 | 0 | [6 empty] | 80 | 5 | 190 | 45 | 290 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 80 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 81 | 80 | 109 | 115 | 100 | 100 | 70
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | ≥6KW系统开启 | 0 | 0 |  |  |  | 0 | 0 | [6 empty] | 80 | 5 | 190 | 45 | 290 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 80 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 81 | 80 | 109 | 115 | 100 | 100 | 70
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | ≥6KW系统开启 | 0 | 0 |  |  |  | 0 | 0 | [6 empty] | 80 | 5 | 190 | 45 | 290 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 80 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 81 | 80 | 109 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
[5 empty] | 斯洛伐克VSD测试设定值 |  | 1 | 1 | 0 |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 斯洛伐克SSE测试设定值 |  | 1 | 1 | 0 |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 1 | 1 | 0 |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | EU-EN50549-1 |  |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  | 捷克 |  |  | 捷克（中压） |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | Czechia | 捷克<=16A系统 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | ≥60000 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1900 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60100 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | Czechia | 捷克>16A系统 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | >100KW系统K值在2-6之间可选 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | ≥60000 | >100KW系统K值在2-6之间可选 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1900 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60100 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 0-5 | ≥0.15s(建议0.2s) | 25 | ≥0.87s(建议1.0s) | 50 | ≥1.76s(建议1.9s) | 85 | ≥3s(建议3.1s) | 0 | 0 | 30000 | 110 | 125 | ≥0.1s(建议0.2s) | 120 | ≥5000 | 115 | ≥60000 | 110 | ≥60000 | 0 | 0 | 30000 | 85 | 110 | 86 | 100 | 109 | 100 | 100 | 100 | 70
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 200 | 25 | 1000 | 50 | 1900 | 85 | 3100 | 0 | 0 | 30000 | 110 | 125 | 200 | 120 | 5050 | 115 | 60100 | 110 | 60100 | 0 | 0 | 30000 | 85 | 110 | 86 | 100 | 109 | 100 | 100 | 100 | 70
[7 empty] | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 32 | [11 empty] | 0 | 0 | [15 empty] | 0 | 0 | 30000 | [19 empty] | 100 | 70
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 |  | 挪威 | 00 | Norway | 挪威 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 0 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 100 | 100 | 70
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[5 empty] | 墨西哥低压测试设定值 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 36-37 | [11 empty] | 0 | 0 | [15 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[6 empty] | ＞25A/16A | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / |  | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | / | / | / | / | / |  | 50 | 0-5 | ≥400 | 25 | ≥1000 | 50 | ≥1850 | 50 | ≥3000 | 0 | 0 | 30000 | 120 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 120 | / | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
[7 empty] | 1 | 1 | 0 | 0 | 0 | / | 0 | 0 |  | / | / | / | / |  | 90 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[7 empty] | 1 | 1 | 0 | 0 | 0 | / | 0 | 0 |  | / | / | / | / |  | 90 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 泰国PEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 大于500KW系统，需要开启 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[5 empty] | 泰国MEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 3 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 109 | / | 100 | 100 | 70
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 41 | [11 empty] | 0 | 0 | [15 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
902 | 43 | [11 empty] | 0 | 0 | [15 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 1MW以上系统开启 | 1MW以上系统开启 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 100 | 100 | 70
902 | 44 | 南非 | 00 | SA | 南非 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[13 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
902 |  | 南非 | 01 | SA-HV | 南非-高压 | [7 empty] | 0 | 0 | [36 empty] | 100 | 100 | 70
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | 由用户或电站确认 |  |  |  |  | 1 |  | 0 | [6 empty] | 90 | 0 | ≥150 | 25 | ≥695 | 60 | ≥1456 | 85 | ≥20000 | 2.5 | 0 |  | 110 | 120 | ≥2000 | / | / | / | / | / | / | 3 | 0 |  |  |  | 91 | 90 | 109 | 110 |  | 100 | 70
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 90 | 0 | 150 | 25 | 695 | 60 | 1456 | 85 | 20000 | 2.5 | 0 | 30000 | 110 | 120 | 2000 | 118 | 5050 | 115 | 60050 | 110 | 60100 | 3 | 0 | 30000 | 50 | 120 | 91 | 90 | 109 | 110 | 100 | 100 | 70
902 | 45 | [11 empty] | 0 | 0 | [15 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[5 empty] | 迪拜安规标准 | 1kV以下 | ≥10KW开启，＜10KW不开启 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 85 | 5 | ≥200 | 45 | ≥400 | [21 empty] | 86 |  | 114 |  | 100 | 100 | 70
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 85 | 5 | 300 | 45 | 500 | 45 | 500 | 45 | 500 | 0 | 0 | 30000 | 115 | 125 | 110 | 120 | 510 | 115 | 2310 | 115 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 1 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | 1 | 85 | 5 | ≥200 | 25 | ≥500 | 55 | ≥950 | 75 | ≥1400 | [17 empty] | 86 |  | 114 |  | 100 | 100 | 70
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 85 | 5 | 300 | 25 | 600 | 55 | 1100 | 75 | 1500 | 0 | 0 | 30000 | 115 | 125 | 110 | 120 | 510 | 115 | 2310 | 115 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
902 | 47-106 | [11 empty] | 0 | 0 | [15 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 1 | 1 | 0 |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 440 | 25 | 1040 | 50 | 1890 | 85 | 3090 | 0 | 0 | 30000 | 110 | 125 | 160 | 120 | 5090 | 110 | 60090 | 115 | 60090 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
[7 empty] | 1 | 1 |  |  |  |  | 0 | 0 | [5 empty] | 3 | [28 empty] | 109 |  | 100 | 100 | 70
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 440 | 25 | 1040 | 50 | 1890 | 85 | 3090 | 0 | 0 | 30000 | 110 | 125 | 160 | 120 | 5090 | 110 | 60090 | 115 | 60090 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
902 | 110 | [11 empty] | 0 | 0 | 0 |  |  |  |  | 0 | [9 empty] | 0 | 0 | 30000 | [9 empty] | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 114 | 115 | 100 | 100 | 70
[5 empty] | 哥伦比亚安规标准 |  | 0 | 0 | 0 |  |  |  | 0 | 0 | [5 empty] | 0 | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 100 | 100 | 70
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 15 | 150 | 25 | 560 | 50 | 1575 | 80 | 2800 | 0 | 0 | 30000 | 110 | 125 | 1000 | 120 | 50000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 110 | 100 | 100 | 70
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 15 | 150 | 25 | 560 | 50 | 1575 | 80 | 2800 | 0 | 0 | 30000 | 110 | 125 | 1000 | 120 | 50000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 110 | 100 | 100 | 70
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | / | / | / | / | / | / | 0 | 0 | / | / | / | / | / |  | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | / | 100 | 70
902 | 112 | 智利 | 00 | Chile | 智利 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 15 | 150 | 25 | 560 | 50 | 1575 | 80 | 2800 | 0 | 0 | 30000 | 110 | 125 | 1000 | 120 | 50000 | 115 | 60000 | 110 | 60000 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 110 | 100 | 100 | 70
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 90 | 4 | 2000 | 25 | 2000 | 50 | 2000 | 75 | 2000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 91 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | 客户需求参考EU-EN50549 | [8 empty] | 0 | 0 | [34 empty] | 109 |  | 100 | 100 | 70
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | 客户需求参考EU-EN50549 | [8 empty] | 0 | 0 | [32 empty] | 51 |  | 119 |  | 100 | 100 | 70
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 4 | 400 | 25 | 1000 | 50 | 1850 | 50 | 3000 | 0 | 0 | 30000 | 120 | 125 | 120 | 120 | 5050 | 120 | 60050 | 120 | 60100 | 0 | 0 | 30000 | 50 | 120 | 51 | 50 | 119 | 120 | 100 | 100 | 70
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 4 | 400 | 25 | 1000 | 50 | 1850 | 75 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 115 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 86 | 85 | 109 | 115 | 100 | 100 | 70
|  |  |  | AnnexC_EN 50549-2 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 0-5 | ≥250(默认400) | 25 | ≥1000 | 50 | ≥1850 | 85 | ≥3000 | 0 | 0 | 30000 | 110 | 125 | ≥120 | 120 | ≥5000 | 120 | ≥60000 | 110 | ≥60000 | 0 | 0 | 30000 | 50 | 120 | 91 | 100 | 109 | 100 | 100 | 100 | 70
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 90 | 4 | 400 | 25 | 1000 | 50 | 1850 | 85 | 3000 | 0 | 0 | 30000 | 110 | 125 | 120 | 120 | 5050 | 120 | 60050 | 110 | 60100 | 0 | 0 | 30000 | 50 | 120 | 91 | 100 | 109 | 100 | 100 | 100 | 70

## ISO孤岛参数
安规库版本 | 安规编号 | 国家 | 标准地区编码 | 标准名称 | 标准中文名称 | 参数说明 | Bit0：孤岛使能寄存器 | Bit1：单相孤岛使能（用于三相逆变器） | Bit0：绝缘阻抗使能寄存器 | Bit1：接地检测使能寄存器 | Bit0：离网PEN短接使能位 | Bit1：N线检测使能位 | Bit0：孤岛使能寄存器 Bit1：单相孤岛使能（用于三相逆变器）总使能位（自动生成） | GFCIConfig Bit0：GFCI使能寄存器 | IslandConfig Bit0：绝缘阻抗使能寄存器 Bit1：接地检测使能寄存器 不需要填写 | InsulationProtectionValue | IsoLeakageCurrentLimit | GFCILimit | PE_N_Config PE和N控制寄存器 Bit0：离网PEN短接使能位 总使能位(自动生成) | SpecialCertification
[15 empty] | Bit0：孤岛使能寄存器 Bit1：单相孤岛使能（用于三相逆变器） | 绝缘阻抗保护值 | 组件对地泄露电流限制 | 漏电流限制（暂不开放，设置无效） | Bit0：离网PEN短接使能位 Bit1：N线检测使能位 | Bit0:以电池功率计算有功、无功
[6 empty] | 精度（自动转换，本文档填写时请忽略） | [9 empty] | 1 | 1 | 1
902 |  |  |  | 参数单位 | 参数单位 | 单位（对应文档中的数值） | [9 empty] | kΩ | mA | mA/kVA
[6 empty] | 1.正标；2.系统电压小于1kV；3.如容量≤135kW则无需考虑电压 | 1 |  |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 00 | 德国 | 00 | VDE4105 | 德国4105 |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 旧4110标准 | 1 |  |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 00 | 德国 | 01 | BDEW | 德国BDEW |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 德国该标准已撤销 | 1 |  |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 00 | 德国 | 02 | VDE0126 | 德国0126 |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 德国 | 03 | VDE4105-HV | 德国4105-高压 | [14 empty] | 0
0
902 |  | 德国 | 04 | BDEW-HV | 德国BDEW-高压 | [14 empty] | 0
[6 empty] | 1、正标；2、系统电压＞1kV至＜60kV公用三相电网； 3、仅适用于达到36MW≥PAmax≥135 kW的最大有功功率。 | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 00 | 德国 | 05 | VDE4110 | 德国4110 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 1、正标；2、系统电压＞60kV公用三相电网； 3、最大有功功率PAmax≥36MW | 1 |  |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 00 | 德国 | 06 | VDE4120 | 德国4120 |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 1、正标 2、系统电压在1KV-150KV之间 3、输出功率≤11KW | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 01 | 意大利 | 00 | CEI-021In. | 意大利(0-21)内部 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 1、正标 2、系统电压≤1KV | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 01 | 意大利 | 01 | CEI-016 | 意大利(0-16) |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 1、正标 2、系统电压在>1KV,≤150KV之间 3、输出功率>11KW | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 01 | 意大利 | 02 | CEI-021Ex. | 意大利(0-21)外部 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | Areti地区的标准，现已和CEI-021In标准一致 | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 01 | 意大利 | 03 | CEI-021Ar. | 意大利(0-21)Areti |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 意大利 | 04 | CEI-021In.-HV | 意大利(0-21)内部-高压 | [14 empty] | 0
[7 empty] | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 01 | 意大利 | 05 | CEI-016-HV | 意大利(0-16)-高压 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[7 empty] | 0 |  |  |  | 0 | 1 | 0 |  | 0 |  |  |  | 2 | 0
902 | 01 | 意大利 | 06 | CEI-016-MV | 意大利(0-16)-中压 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 0 |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 02 | 澳洲 | 00 | Australia | 澳大利亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | 2 | 0
902 | 02 | 澳洲 | 08 | Australia-B | 澳大利亚-B |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | ASNZS4777.2-2020 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | 2 | 0
902 | 02 | 澳洲 | 09 | Australia-C | 澳大利亚-C |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 澳洲 | 10 | AU-SA-HV | 南澳-高压 | [14 empty] | 0
0
902 |  | 澳洲 | 11 | Australia-MV | 澳大利亚-中压 | [14 empty] | 0
|  |  |  | RD1699 | 西班牙 | 西班牙户用储能（与UNE217002一起出） | 1 | 0 |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 03 | 西班牙 | 00 | ESP-RD1699 | 西班牙 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 西班牙 | 01 | RD1699-HV | 西班牙-高压 | [14 empty] | 0
|  |  |  | NTS | 西班牙 | 电站标准； 1、Type A:系统电压＜110 kV；最大容量为≥0.8 kW至≤100 kW； 2、Type B：系统电压＜110 kV；最大容量为＞100 kW至≤5 MW； 3、Type C：系统电压＜110 kV；最大容量为＞5 MW至≤50 MW； 4、Type D：系统电压≥110 kV；最大容量为＞50 MW. | 1 | 0 | 1 | 0 | 0 | 1 | 1 |  | 1 |  |  |  | 2 | 0
902 | 03 | 西班牙 | 02 | NTS | 西班牙NTS |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | UNE217002+RD647 | 西班牙UNE+RD | 西班牙户用储能 | 1 | 0 |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 03 | 西班牙 | 03 | UNE217002+RD647 | 西班牙UNE+RD |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | Spain island | 西班牙island |  | 1 | 0 |  |  | 0 | 1 | 1 |  | 0 |  |  |  | 2 | 0
902 | 03 | 西班牙 | 04 | Spain island | 西班牙island |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | 非标低压安规文件 | 1 | 0 | 1 | 0 | 0 | 1 | 1 |  | 1 | / | / | / | / | 0
902 | 03 | 西班牙 | 05 | RD1699-LV | 西班牙-低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 04 | 土耳其 | 00 | Turkey | 土耳其 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 05 | 丹麦 | 00 | Denmark | 丹麦 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | TR3.2.2并网 |  | 1、正标 2、＞11KW系统 A2. Plants above 11 kW up to and including 50 kW B. Plants above 50 kW up to and including 1.5 MW C. Plants above 1.5 MW up to and including 25 MW D. Plants above 25 MW or connected to over 100 kV. | 1 | 0 |  |  | 0 | 1 | 1 | 1 | 0 | / | / | / | 2 | 0
902 | 05 | 丹麦 | 01 | DK-TR322 | 丹麦TR322 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 05 | 丹麦 | 02 | Western Denmark | 丹麦西部 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 05 | 丹麦 | 03 | Eastern Denmark | 丹麦东部 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | VDE0126(Greece Continent) |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | 2 | 0
902 | 06 | 希腊大陆 | 00 | GR-Cont. | 希腊大陆 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | VDE0126(Greece island) |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | 2 | 0
902 | 06 | 希腊大陆 | 01 | GR-Island | 希腊岛屿 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 07 | 荷兰 | 00 | Netherland | 荷兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 荷兰 | 01 | Netherland-MV | 荷兰-中压 | [14 empty] | 0
0
902 |  | 荷兰 | 02 | Netherland-HV | 荷兰-高压 | [14 empty] | 0
|  |  |  | C10/11 | 比利时 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 08 | 比利时 | 00 | Belgium | 比利时 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 比利时 | 01 | Belgium-HV | 比利时-高压 | [14 empty] | 0
[6 empty] | 非标低压安规文件 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 08 | 比利时 | 02 | Belgium-LV | 比利时-低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | UK-G99标准 |  |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 09 | 英国 | 00 | UK-G99 | 英国G99 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | UK-G98标准 |  |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 09 | 英国 | 01 | UK-G98 | 英国G98 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 英国 | 02 | UK-G99-HV | 英国G99-高压 | [14 empty] | 0
|  |  |  | NB/T 32004-2018 | 中国 |  | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2 | 0
902 | 10 | 中国 | 00 | China | 中国 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | CNS+15382-2018 | / |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | 2 | 0
902 | 10 | 中国 | 01 | Taiwan | 台湾 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | NB/T 32004-2018 |  |  | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2 | 0
902 | 10 | 中国 | 02 | TianHe | 天合富家 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 | 10 | 中国 | 03 | HongKong | 香港（220V） |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[11 empty] | 0 | 1 | [6 empty] | 2 | 0
902 | 10 | 中国 | 04 | SKYWORTH | 创维 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | NB/T 32004-2018 | 中国CQC B类 |  | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2 | 0
902 | 10 | 中国 | 05 | CSISolar | 阿特斯 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[11 empty] | 0 | 1 | [6 empty] | 2 | 0
902 | 10 | 中国 | 06 | CHINT | 正泰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 中国 | 07 | China-MV | 中国-中压 | [14 empty] | 0
0
902 |  | 中国 | 08 | China-HV | 中国-高压 | [14 empty] | 0
|  |  |  | NB/T 32004-2018 | 中国CQC A类 |  | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2 | 0
902 | 10 | 中国 | 09 | China | 中国 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 中国CQC B类 |  | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2 | 0
902 | 10 | 中国 | 10 | JOLYWOOD | 中来 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[7 empty] | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2 | 0
902 | 10 | 中国 | 11 | RISEN | 东方日升 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 中国CQC B类 |  | 1 | / | 1 | / | 0 | 1 |  | 1 |  |  |  |  | 2
902 | 10 | 中国 | 12 | China-wide | 中国宽范围电压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | France | 法国VDE0126 | 2024年会失效 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | / | / | / | / | / | 2 | 0
902 | 11 | 法国 | 00 | France | 法国 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | FRArrete23 | 法国Arrete23 |  | 1 | 0 | 1 | 0 | 0 | 1 | / | / | / | / | / | / | 2 | 0
902 | 11 | 法国 | 01 | FRArrete23 | 法国Arrete23 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 法国 | 02 | FR VDE0126-HV | 法国-高压 | [14 empty] | 0
|  |  |  | France VFR 2019 | 法国VFR 2019 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | / | / | / | / | / | 2 | 0
902 | 11 | 法国 | 03 | France VFR 2019 | 法国VFR 2019 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | France | 法国VDE0126 | Enedis客户 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | / | / | / | / | / | 2 | 0
902 | 11 | 法国 | 04 | VDE0126 Enedis | 法国 Enedis |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 法国 | 05 | VDE0126-HV Enedis | 法国-高压 Enedis | [14 empty] | 0
|  |  |  | France VFR 2019 | 法国VFR 2019 | Enedis客户 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | / | / | / | / | / | 2 | 0
902 | 11 | 法国 | 06 | VFR2019 Enedis | 法国VFR2019 Enedis |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | France EN50549-1 | 法国EN50549-1 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 11 | 法国 | 07 | France EN50549-1 | 法国EN50549-1 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | France EN50549-2 | 法国EN50549-2 | 法国新要求, 目前和VDE 0126同时都在使用 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 11 | 法国 | 08 | France EN50549-2 | 法国EN50549-2 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | Poland | 波兰A | 1、正标 2、A≤0.2MW的系统 | 1 | 0 | 1 |  | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 12 | 波兰 | 00 | Poland | 波兰A |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 波兰 | 01 | Poland-MV | 波兰-中压 | [14 empty] | 0
0
902 |  | 波兰 | 02 | Poland-HV | 波兰-高压 | [14 empty] | 0
|  |  |  | Poland | 波兰ABCD | 1、正标 2、B是0.2-10MW的系统，C＞75MW系统 | 1 | 0 | 1 |  | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 12 | 波兰 | 03 | Poland | 波兰ABCD |  | 1 | 0 | 1 |  | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 奥地利TOR安规标准 | 1、正标 2、Tor Erzeuger TypeA： ＜250kW and nominal voltage＜110kV Tor Erzeuger TypeB：maximum capacity ≥250KW and <35MV and nominal voltage <110KV | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 13 | 奥地利 | 00 | Tor Erzeuger | 奥地利TOR |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 14 | 日本 | 00 |  |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 | 15 | 瑞士 | 00 | Switzerland Type A | 瑞士 Type A |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 | 15 | 瑞士 | 01 | Switzerland Type B | 瑞士 Type B |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 16-17 | [18 empty] | 0
[6 empty] | 被 EN50549替代 | 1 | 0 | 1 |  | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 18 | 欧洲EU | 00 | EU-EN50438 | 欧洲-EN50438 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  | 1、正标 2、 Rfg的Type划分如下，EN 50549-1根据TypeA和TypeB制定： --(a) 110 千伏以下的连接点，最大容量为 0.8 千瓦或以上(A 类)； --(b) 连接点低于 110 千伏，最大容量达到或超过各相关 TSO 根据第 3 款规定的程序提出的阈值（B 型）。该阈值不得高于表 1 所载 B 型发电模块的限值； --(c) 连接点低于 110 千伏，最大容量达到或超过每个相关的 "电网运行规 范 "根据第 3 款规定的阈值(C 类)。该阈值不得高于表 1 所载 C 型发电模块的限值；或 --(d) 110 千伏或以上的连接点（D 型）。如果发电组件的连接点低于 110 千伏，而其最大容量达到或超过第 3 段规定的阈值，则该发电组件也属于 D 型。该临界值不得高于表 1 所载的 D 型发电组件的限值。 • 低压配电网: Un≤1kV | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 18 | 欧洲EU | 01 | EU-EN50549 | 欧洲-EN50549 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 欧洲EU | 02 | EU-EN50549-HV | 欧洲-EN50549-高压 | [14 empty] | 0
|  | 欧洲通用 |  | EN 50549-2 | 欧洲-EN50549-2 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 18 | 欧洲EU | 03 | EU-EN50549-2 | 欧洲-EN50549-2 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | IEC EN61727 | 欧洲-IEC EN61727 |  | 1 | 0 | / | / | 0 | 1 | 1 | / |  | / | / | / | 2 | 0
902 | 19 | IEC EN61727 | 00 | IECEN61727 | 欧洲-IEC EN61727 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | / | / |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 20 | 韩国 | 00 | Korea | 韩国 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 20 | 韩国 | 01 | Korea-DASS | 韩国DASS | 特殊用户参数，暂无标准 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EN50549-1 | / |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 21 | 瑞典 | 00 | Sweden | 瑞典 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 22 | 欧洲通用 | 00 | EU General | 欧洲通用 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 欧洲通用 | 01 | EU General-MV | 欧洲通用-中压 | [14 empty] | 0
0
902 |  | 欧洲通用 | 02 | EU General-HV | 欧洲通用-高压 | [14 empty] | 0
902 | 23 | [5 empty] | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[7 empty] | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 24 | 塞浦路斯 | 00 | Cyprus | 塞浦路斯 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 塞浦路斯等级A | 0 < P < 10.4kWp | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | / | / | / | / | 2
902 | 24 | 塞浦路斯 | 01 | CY-LV-RES | 塞浦路斯等级A |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 塞浦路斯等级B | 10.4kWp < P < 120kWp | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | / | / | / | / | 2
902 | 24 | 塞浦路斯 | 02 | CY-LN/MV-COM | 塞浦路斯等级B |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 塞浦路斯等级C | P > 120kWp | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | / | / | / | / | 2
902 | 24 | 塞浦路斯 | 03 | CY-LV/MV-UT | 塞浦路斯等级C |  | 1 | 1 | 1 | 0 | 0 | 1 | 3 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  | 00 | IEC61727 | 印度-IEC61727 |  | 1 | 0 | / | / | 0 | 1 | 1 | / |  | / | / | / | 2 | 0
902 | 25 | 印度 | 00 | India | 印度 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 印度 | 01 | India-MV | 印度-中压 | [14 empty] | 0
0
902 |  | 印度 | 02 | India-HV | 印度-高压 | [14 empty] | 0
|  |  |  | CEA | 印度-CEA | 印度电力管理局要求 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | / | / | / | 2 | 0
902 | 25 | 印度 | 03 | CEA | 印度CEA |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | IEC 61727-LV | 印度IEC61727-LV | 非标低压安规文件（用于低压区域，如巴西、菲律宾等） | 1 | 0 | / | / | 0 | 1 | 1 | / |  | / | / | / | 2 | 0
902 | 25 | 印度 | 04 | India-LV | 印度-低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | Kerala地区安规参数 | 1 | 0 | / | / | 0 | 1 | 1 | / |  | / | / | / | 2 | 0
902 | 25 | 印度 | 05 | India-Kerala | 印度-Kerala |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  | 00 | PHI | 菲律宾 | 1、正标 2、1.Large Conventional:Conventional Embedded Generating Plant with anaggregated Installed Capacity of 10 MW or more. 2.Large VRE:VRE Embedded Generating Plant with an aggregatedInstalled Capacity of 10 MW or more. 3.Medium:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 1 MW which do not qualifyas Large Embedded Generating Plant. 4.Intermediate:Conventional or VRE Embedded Generating Plants withInstalled Capacity larger than 100 kW and equal to or lessthan 1 MW:and Conventional Embedded Generating Plants with InstalledCapacity lower or equal to 100 kW connected to MVonetworks. 5.Small:Embedded Generating Plant with Installed Capacity largerthan 10 kW and equal to or less than 100 kW connected toLV networks. 6.Micro:Embedded Generating Plants with Installed Capacitylower or equal to 10 kW connected to LV networks. |  |  |  |  | 0 | 1 | 0 |  | 0 | / | / | / | 2 | 0
902 | 26 | 菲律宾 | 00 | PHI | 菲律宾 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 菲律宾 | 01 | PHI-MV | 菲律宾-中压 | [14 empty] | 0
[7 empty] | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 26 | 菲律宾 | 02 | PHI-LV | 菲律宾-低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  | 00 | ASNZS4777.2-2020 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 |  |  |  | 2 | 0
902 | 27 | 新西兰New Zealand | 00 | NewZealand | 新西兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 新西兰New Zealand | 01 | NewZealand-MV | 新西兰-中压 | [14 empty] | 0
0
902 |  | 新西兰New Zealand | 02 | NewZealand-HV | 新西兰-高压 | [14 empty] | 0
|  |  |  | PORTARIA Nº 140 | 巴西安规标准 | 1、正标 2、0-75kW逆变器, 储能逆变器,离网逆变器必须要符合PORTARIA Nº 140, 75kW以上同样适用但是不做强制要求. | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 28 | Brazil(巴西) | 00 | PORTARIA Nº 140 | 巴西 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | PORTARIA Nº 140 | 巴西低压安规标准 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 28 | Brazil(巴西) | 01 | Brazil-LV | 巴西低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | PORTARIA Nº 140 | 巴西230V安规标准 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 28 | Brazil(巴西) | 02 | Brazil-230 | 巴西230 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | PORTARIA Nº 140 | 巴西254V安规标准 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 28 | Brazil(巴西) | 03 | Brazil-254 | 巴西254 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | Brazil(巴西) | 04 | Brazil-288 | 巴西288 | [14 empty] | 0
[5 empty] | 斯洛伐克VSD测试设定值 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 29 | 斯洛伐克slovakia VSD(29) | 00 | SK-VSD | 斯洛伐克VSD |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 斯洛伐克SSE测试设定值 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 29 | slovakia SSE(30) | 01 | SK-SSE | 斯洛伐克SSE |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 斯洛伐克ZSD测试设定值 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 29 | slovakia ZSD(31) | 02 | SK-ZSD | 斯洛伐克ZSD |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EU-EN50549-1 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 30 | 捷克 | 00 | Czechia | 捷克 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  | 捷克 |  |  | 捷克（中压） |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 30 | 捷克 | 01 | Czechia-MV | 捷克（中压） |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | Czechia | 捷克<=16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 30 | 捷克 | 02 | Czechia | 捷克<=16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | Czechia | 捷克>16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 30 | 捷克 | 03 | Czechia | 捷克>16A系统 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | Czechia PPDS 2023 | 捷克 PPDS 2023 | ≥0.8kW且＜100kW | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 30 | 捷克 | 04 | Czechia PPDS 2023 | 捷克 PPDS 2023 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[7 empty] | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 31 | 斯洛文尼亚 | 00 | SIST EN 50549-1 | 斯洛文尼亚50549 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 32 | [14 empty] | 50 | 20 | 0 |  | 0
902 | 33 | 乌克兰 | 00 | Ukraine | 乌克兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 |  | 挪威 | 00 | Norway | 挪威 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 挪威低压测试设定值 | 非标低压安规文件 | 1 | [8 empty] | / | / | / |  | 0
902 | 34 | 挪威 | 01 | Norway-LV | 挪威低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 墨西哥低压测试设定值 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | / | / | / | 2 | 0
902 | 35 | 墨西哥低压 | 00 | Mexico-LV | 墨西哥低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 36-37 | [14 empty] | 50 | 20 | 0 |  | 0
902 | 38 | 60HZ通用 | 00 | Range-60Hz | 60HZ宽范围安规 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[6 empty] | ＞25A/16A | 1 | 0 | / | / | 0 | 1 | 1 | / |  | / | / | / | 2 | 0
902 | 39 | 爱尔兰 | 00 | Ireland | 爱尔兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EN50549-1 | 爱尔兰 | ＜25A/16A | 1 | 0 | / | / | 0 | 1 | 1 | / |  | / | / | / | 2 | 0
902 | 39 | 爱尔兰 | 01 | Ireland | 爱尔兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 | 39 | 北爱尔兰 | 02 | Nor Ireland G99 | 北爱尔兰G99 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 | 39 | 北爱尔兰 | 03 | Nor Ireland G98 | 北爱尔兰G98 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 泰国PEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, PEA有大于500kW电力系统要求 3、PEA主管的是除曼谷以外其他地区的电力供应 | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 40 | 泰国(PEA) | 00 | Thai-PEA | 泰国PEA |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 泰国MEA标准 | 1、正标 2、PEA与MEA是泰国两家不同的电力公司, 3、MEA主管的是曼谷地区的电力供应 | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 40 | 泰国(MEA) | 01 | Thai-MEA | 泰国MEA |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 41 | [11 empty] | 0 |  | 0 | 50 | 20 | 0 |  | 0
902 |  | 50HZ低压通用 | 00 | LV-50Hz | 50HZ低压通用 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 43 | [11 empty] | 0 |  | 0 | 50 | 20 | 0 |  | 0
|  |  |  | NRS 097-2-1 | 南非标准 | a) Category A1: 0 – 13,8 kVA b) Category A2: 13,8 kVA – 100 kVA c) Category A3: 100 kVA – 1 MVA | 1 | 0 | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 44 | 南非 | 00 | SA | 南非 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
0
902 |  | 南非 | 01 | SA-HV | 南非-高压 | [14 empty] | 0
|  |  |  | SA RPPS of C | 南非+RPPS of Category C | Category C: 20 MVA or higher | 1 | 0 | 1 |  | 0 |  |  |  | 1 | / | / | / |  | 0
902 | 44 | 南非 | 02 | SA RPPS of C | 南非+RPPS of Category C |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 45 | [11 empty] | 0 |  | 0 | 50 | 20 | 0 |  | 0
[5 empty] | 迪拜安规标准 | 1kV以下 | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 46 | 迪拜（低压） | 00 | DEWG | 迪拜 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
[5 empty] | 迪拜-电站安规标准 | 1kV-33kV | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 46 | 迪拜（中压） | 01 | DEWG-MV | 迪拜-电站 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 47-106 | [14 empty] | 50 | 20 | 0 |  | 0
|  |  |  | EN50549-1 | 克罗地亚安规标准 |  | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 107 | 克罗地亚 | 00 | Croatia | 克罗地亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | EN50549-1 | 立陶宛安规标准 |  | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 108 | 立陶宛 | 00 | Lithuania | 立陶宛 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 109 | 爱沙尼亚 | 00 | Estonia | 爱沙尼亚 | 特殊用户参数，暂无标准 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 110 | [14 empty] | 50 | 20 | 0 |  | 0
[5 empty] | 哥伦比亚安规标准 |  | 1 |  | 1 |  | 0 | 1 | 1 |  | 1 | / | / | / | 2 | 0
902 | 111 | 哥伦比亚 | 00 | Columbia | 哥伦比亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 111 | 哥伦比亚 | 01 | Columbia-LV | 哥伦比亚低压 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  | 智利 |  | Chile | 智利 | 给智利电力监督局通过的安规 | 1 | / | / | / | / | / | / | / | / | / | / | / | / | 0
902 | 112 | 智利 | 00 | Chile | 智利 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 121 | 沙特 | 00 | Saudi Arabia | 沙特 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | 客户需求参考EU-EN50549 | [15 empty] | 0
902 | 122 | 拉脱维亚 | 00 | Latvia | 拉脱维亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | 客户需求参考EU-EN50549 | [15 empty] | 0
902 | 123 | 罗马尼亚 | 00 | Romania | 罗马尼亚 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | 客户需求参考EU General |  | 当地经销商要求 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 124 | 突尼斯 | 00 | Tunisia | 突尼斯 |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 50 | 20 | 0 | 2 | 0
|  |  |  | AnnexC_EN 50549-2 |  |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0
902 | 125 | 芬兰 | 00 | Finland | 芬兰 |  | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 50 | 20 | 0 | 2 | 0